## Analyzer House VDR
Vendor Document Requirement (VDR) — Analyzer House / Analyzer Shelter — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Aligned with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP): FAT/iFAT/SAT, witness & hold points | Project Admin & Planning | All | Pressurization tests, HVAC performance, F&G function, electrical tests, PDI | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule & Document Submittal Plan | Project Admin & Planning | All | Milestones with due weeks for drawings & procedures | R | Yes | No | Yes | No
5 | HSE Plan incl. Risk Assessment & Lifting/Handling Plan | Project Admin & Planning | All | Factory & site HSE; method statements; rigging plan | R | Yes | No | Yes | No
6 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
7 | Design Basis & Environmental Conditions | Design Basis & Compliance | All | Ambient temp, humidity, sand/dust, corrosion category, wind, seismic zone | R | Yes | Yes | Yes | No
8 | Hazardous Area Classification & Compliance Strategy | Design Basis & Compliance | Ex sites | Inside: non-hazardous by pressurization; Outside: Zone class; references: IEC 60079-13 / NFPA 496; device selection rules | R | If applicable | Yes | If applicable | No
9 | Compliance Matrix to Project Specifications & Codes | Design Basis & Compliance | All | Point-by-point compliance; listed deviations | R | Yes | Yes | Yes | No
10 | Analyzer House GA Drawings — Plan, Elevations, Sections | Mechanical/Civil/Architectural | All | Overall dimensions, doors/windows, clearances, walkways, roof drainage | R | Yes | Yes | Yes | Yes
11 | Foundation / Skid / Structural Frame Calculations & Drawings | Mechanical/Civil/Architectural | All | Baseplate/skid, lifting lugs, COG, transport; allowable loads | R | Yes | Yes | Yes | Yes
12 | Fire/Blast Rating Declaration & Details (walls/doors/windows) | Mechanical/Civil/Architectural | If specified | UL 1709/BS/EN fire rating; blast resistance if required | R/F | If applicable | If applicable | If applicable | Yes
13 | Doors/Windows/Penetrations Specification | Mechanical/Civil/Architectural | All | Fire/Ex ratings; door switches/alarms; airlock/vestibule if used | R | Yes | Yes | Yes | Yes
14 | Cable Tray/Conduit Layout & Penetration Sealing Details | Mechanical/Civil/Architectural | All | Glands/seals, IP rating, weatherproofing | R | Yes | Yes | Yes | Yes
15 | Sample System Rack Layout & Utilities Routing | Mechanical/Civil/Architectural | All | Analyzer skids, fast loops, vent/flare routing, safety clearances | R | Yes | Yes | Yes | Yes
16 | Materials & Coatings Specification (external & internal) | Mechanical/Civil/Architectural | All | Panel materials, insulation, paint system & DFT | R | Yes | Yes | Yes | Yes
17 | HVAC Heat Load Calculations & Equipment Selection | HVAC/Pressurization/Utilities | All | Internal loads from analyzers/people; sizing; redundancy (N+1) | R | Yes | Yes | Yes | Yes
18 | HVAC Ducting/Layout Drawings & Control Philosophy | HVAC/Pressurization/Utilities | All | Supply/return airflow, filtration, setpoints, alarms, smoke shutdown | R | Yes | Yes | Yes | Yes
19 | Pressurization & Purge System Design (IEC 60079-13 / NFPA 496) | HVAC/Pressurization/Utilities | Ex sites | Leakage rate, purge time, DP setpoint/alarms, door interlocks, airflow measurement | R | If applicable | Yes | If applicable | Yes
20 | Gas Detection Layout & Setpoints | HVAC/Pressurization/Utilities | All | Detector types (flammable/toxic/O₂), placement, alarm levels, calibration points | R | Yes | Yes | Yes | Yes
21 | Cause & Effect (C&E) — F&G / HVAC / Pressurization / ESD | HVAC/Pressurization/Utilities | All | Trip matrix: fans, dampers, purge, door alarms, ESD, power | R | Yes | Yes | Yes | Yes
22 | Vent/Exhaust & Safe Dispersion Plan | HVAC/Pressurization/Utilities | All | Vent locations, backpressure, flame arrestors where required | R | Yes | Yes | Yes | Yes
23 | Utilities Specification — Power, Lighting, Small Power, UPS, Air | HVAC/Pressurization/Utilities | All | UPS autonomy, receptacles, instrument air quality (ISO 8573-1) | R | Yes | Yes | Yes | Yes
24 | Single Line Diagram & Load List | Electrical/Instrumentation | All | Main incomer/UPS, DBs, breakers, fault levels | R | Yes | Yes | Yes | Yes
25 | Power Distribution & Cable Schedule | Electrical/Instrumentation | All | DBs, feeders, cable sizing/derating | R | Yes | Yes | Yes | Yes
26 | Lighting Layout (Normal & Emergency) — Lux Calculations | Electrical/Instrumentation | All | Levels per area/class; emergency duration | R | Yes | Yes | Yes | Yes
27 | Earthing, Bonding & Shielding Scheme | Electrical/Instrumentation | All | PE/FE bars, equipotential bonding, shield termination rules | R | Yes | Yes | Yes | Yes
28 | Control/Alarm Wiring Diagrams & Terminal Schedules | Electrical/Instrumentation | All | F&G, HVAC, purge system, door switches/DP switches | R | Yes | Yes | Yes | Yes
29 | Bill of Materials — Shelter/HVAC/Purge/F&G/Electrical | Electrical/Instrumentation | All | Part nos., materials, ratings, firmware/HW revisions where relevant | R | Yes | Yes | Yes | Yes
30 | HVAC Commissioning & Air Balancing Procedure | Procedures & QC | All | Flow measurement method, setpoint tuning, acceptance criteria | R/W | Yes | If requested | Yes | Yes
31 | Room Pressurization / Purge Test Procedure | Procedures & QC | Ex pressurized | Leak test, purge time, DP alarms, door interlock checks | R/W | If applicable | If applicable | If applicable | Yes
32 | F&G Functional Test Procedure & Detector Calibration | Procedures & QC | All | Bump/cal gas methods, setpoints, inhibit/vote handling | R/W | Yes | If requested | Yes | Yes
33 | Electrical Pre-commissioning (IR/Continuity/Earth) Procedure | Procedures & QC | All | Test instruments & acceptance criteria | R/W | Yes | If requested | Yes | Yes
34 | Painting/Coating Procedure & DFT Plan | Procedures & QC | If painted/coated | System, prep class, DFT gauges & hold points | R | If applicable | If applicable | If applicable | Yes
35 | WPS/PQR/Welder Qualification — Structural/Skid | Procedures & QC | If welded items | Procedure & welder qualifications | R | If applicable | If applicable | If applicable | Yes
36 | Pressurized Room Compliance (IEC 60079-13 / NFPA 496) Statement | Compliance & Certificates | Ex pressurized | Design & test compliance; any third-party assessment | F | If applicable | If applicable | If applicable | Yes
37 | ATEX/IECEx Certificates — Purge Panel, Barriers, Detectors | Compliance & Certificates | Ex equipment | Schedules & entity parameters; installation conditions | R/F | If applicable | If applicable | If applicable | Yes
38 | Ingress Protection (IP/NEMA) Declarations | Compliance & Certificates | Enclosures/doors/penetrations | IEC 60529/NEMA | F | Yes | No | Yes | Yes
39 | EMC/EMI Compliance (IEC 61326 or relevant) | Compliance & Certificates | Electrical devices | Industrial environment | F | If applicable | If applicable | If applicable | Yes
40 | Electrical Safety (IEC 61010-1/61439 as applicable) | Compliance & Certificates | Panels/devices | Safety of electrical equipment/switchgear | F | If applicable | If applicable | If applicable | Yes
41 | Fire Rating Certificates — Walls/Doors/Windows | Compliance & Certificates | If fire-rated design | UL/BS/EN evidence with durations | F | If applicable | If applicable | If applicable | Yes
42 | Seismic / Wind Qualification (if specified) | Compliance & Certificates | If required by project | IEC/IEEE 344 or local code | F | If applicable | If applicable | If applicable | Yes
43 | Civil Defense / Authority Approval (e.g., QCDD) | Compliance & Certificates | If jurisdiction requires | Approval letters or permits | F | If applicable | If applicable | If applicable | Yes
44 | Mill Test Certificates (EN 10204 3.1) — Structural/Skid/fasteners | Materials & Special | Structural/welded | Steel grades & fasteners | F | If applicable | If applicable | If applicable | Yes
45 | Cables, Ducts, Insulation & Panel Material Certificates | Materials & Special | As specified | Material data sheets & CoCs | F | If applicable | If applicable | If applicable | Yes
46 | HVAC Performance & Air Balancing Report | Inspection & Test Records | All | Measured flows, temps, setpoint achievement | F/W | Yes | No | Yes | Yes
47 | Room Pressurization / Purge Test Report | Inspection & Test Records | Ex pressurized | Leakage rate, purge time, DP alarms, door interlocks results | F/W | If applicable | No | If applicable | Yes
48 | F&G Functional Test & Calibration Certificates | Inspection & Test Records | All | Detector calibration & bump tests; C&E results | F/W | Yes | No | Yes | Yes
49 | Electrical Test Certificates (IR/Continuity/Earth/Loop) | Inspection & Test Records | All | Test logs & instruments certs | F | Yes | No | Yes | Yes
50 | Illumination Level Measurement Report | Inspection & Test Records | All | Lux levels vs calculations | F | If applicable | If applicable | If applicable | Yes
51 | Noise Level Measurement Report | Inspection & Test Records | If specified | dBA inside & outside | F | If applicable | If applicable | If applicable | Yes
52 | Painting/Coating DFT & Holiday Test Reports | Inspection & Test Records | If painted/coated | Measured DFT; holiday tests if required | F | If applicable | If applicable | If applicable | Yes
53 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
54 | IOM Manuals — Shelter, HVAC, Purge System, Gas Detection, UPS | Manuals & O&M | All | Install, operation, maintenance, troubleshooting | F | Yes | No | Yes | Yes
55 | Maintenance Schedule & Spare Parts List | Manuals & O&M | All | Critical spares & intervals | F | Yes | No | Yes | Yes
56 | Training Plan & Materials (Operator/Maintenance) | Manuals & O&M | If specified | Agendas, handouts, attendance | F | If applicable | If applicable | If applicable | Yes
57 | As-built Drawings — GA/Structural/HVAC/Electrical/F&G/C&E | As-built & Close-out | All | PDF + native files | F | Yes | No | Yes | Yes
58 | As-built Configuration & Parameter Lists | As-built & Close-out | All | HVAC setpoints, DP setpoints, detector IDs/locations, alarm levels | F | Yes | No | Yes | Yes
59 | Serial Number-to-Tag/Equipment Cross-Reference | As-built & Close-out | All | Fans, AHUs, purge panel, detectors, DBs with firmware where applicable | F | Yes | No | Yes | Yes
60 | Warranty Certificates | As-built & Close-out | All | Coverage & start date | F | Yes | No | Yes | Yes
61 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files | F | Yes | No | Yes | Yes
62 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
63 | Pre-delivery Inspection (PDI) Checklist & Photos | Packing & Logistics | All | Internal photos, labels, wiring tidiness | F | Yes | No | Yes | Yes
64 | Preservation & Packing Records with Photos | Packing & Logistics | All | Desiccants, shock/tilt indicators, protective coverings | F | Yes | No | Yes | Yes
65 | Shipping & Handling Instructions | Packing & Logistics | All | Lifting points, tie-down, storage, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Analyzer House / Analyzer Shelter VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the scope requires (e.g., Ex pressurized room, fire/blast rating, seismic, special jurisdiction approvals).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: GA & structural, HVAC load & layout, pressurization/purge design, gas detection layout & C&E, power/lighting & earthing, penetration sealing, sample rack layout, compliance matrix, and declarations for IP/EMC/Ex (as applicable).
4) Standards reference (typical): IEC 60079-13 & NFPA 496 (pressurized rooms), IEC 60079-0/-11 for Ex devices, IEC 61326 (EMC), IEC 60529 (IP), IEC 61010-1/61439 (electrical safety), NFPA 70/NEC, BS/EN/UL fire ratings, ISO 8573-1 (instrument air).
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/calcs/procedures — 3–5 weeks; FAT/iFAT procedures — 4 weeks; Final records — prior to shipment.
6) MRB content should include: HVAC/performance & pressurization test reports, F&G functional results, electrical test certificates, conformance certificates (Ex/IP/EMC/fire/seismic as applicable), materials certificates, manuals, as-built drawings/configuration, PDI photos, and packing list.