## CEMS VDR
Vendor Document Requirement (VDR) — Continuous Emission Monitoring System (CEMS: CO₂ / CO / NOx / SO₂ / O₂) — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Aligned with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. FAT/iFAT/SAT, witness & hold points | Project Admin & Planning | All | Performance/QAL tests, analyzer calibration, leak/pressure, DAHS checks | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly / Software Build Schedule | Project Admin & Planning | All | Milestones and submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Design Basis & Measurement Objectives | Design Basis & Compliance | All | Pollutants: CO₂ / CO / NOx / SO₂ / O₂; averaging periods, reporting basis (dry/wet, normalized), units | R | Yes | Yes | Yes | No
7 | Compliance Matrix to Regulations/Standards | Design Basis & Compliance | All | EN 14181 (QAL2/QAL3), EN 15267 (QAL1), EN 15259 (measurement sections), ISO 12039 (CO/CO₂), EN 14792 (NOx), EN 14791 (SO₂), EPA 40 CFR Pt 60/75 PS-2/3/4 (if applicable) | R | Yes | Yes | Yes | No
8 | Site/Stack Survey & Sampling Location Suitability | Design Basis & Compliance | All | Port locations, straight-run, platforms; per EN 15259 | R | Yes | Yes | Yes | No
9 | CEMS System Architecture Diagram | System Architecture & Method | All | Analyzer(s), sample system, heated lines, DAHS, network, interfaces | R | Yes | Yes | Yes | Yes
10 | Measurement Principle & Analyzer Selection | System Architecture & Method | All | NDIR (CO/CO₂/SO₂), UV (SO₂), Chemiluminescence (NOx), Paramagnetic/ZrO₂ (O₂), dilution vs hot-wet extractive; redundancy/auto-switching | R | Yes | Yes | Yes | Yes
11 | Ranges, Resolution, Accuracy & Response Time | System Architecture & Method | All | Span ranges per pollutant; LOD; T90; drift; cross-interference handling | R | Yes | Yes | Yes | Yes
12 | QAL1 Certificates (EN 15267) — per analyzer model | System Architecture & Method | EU/EN compliance | Provide copies with certificate numbers & application ranges | R/F | If applicable | Yes | If applicable | Yes
13 | Cross-Interference & Moisture Effects Assessment | System Architecture & Method | All | H₂O, CO₂ effects on NDIR; NO₂/NOx converter efficiency; SO₂ UV interferences | R | Yes | Yes | Yes | Yes
14 | Heated Sample Line Specification & Routing | System Architecture & Method | Extractive systems | Temp setpoint, length, power, insulation, installation details | R | If applicable | Yes | If applicable | Yes
15 | Sample Probe & Filter Assembly Design | Sample System & Conditioning | All | Heated probe, blowback; filter type/mesh; materials; position | R | Yes | Yes | Yes | Yes
16 | Sample Conditioning System P&ID / Hook-up | Sample System & Conditioning | Extractive systems | Coolers/permeation dryers, pumps, condensate handling, moisture measurement, flow control, bypass/vent | R | If applicable | Yes | If applicable | Yes
17 | Dilution Extractive System Details | Sample System & Conditioning | If dilution used | Dilution ratio, air purity, critical orifice, control & verification | R | If applicable | Yes | If applicable | Yes
18 | Hot-wet Basis Strategy (no drying) | Sample System & Conditioning | If hot-wet | High-temp path, corrosion control, water vapor correction approach | R | If applicable | Yes | If applicable | Yes
19 | Backpurge/Blowback & Filter Maintenance Plan | Sample System & Conditioning | All | Compressed air quality, intervals, controls interlocks | R | Yes | Yes | Yes | Yes
20 | Materials of Construction (wetted & non-wetted) | Sample System & Conditioning | All | Probe/filters/tubing/seals; corrosion & temp ratings | R | Yes | Yes | Yes | Yes
21 | Calibration & Validation Strategy | Calibration / QA | All | Zero/span gases; frequency; drift limits; converter efficiency (NOx); audit trail | R | Yes | Yes | Yes | Yes
22 | Calibration Gas Specifications & Manifolds | Calibration / QA | All | ISO/IEC 17025 traceability; concentrations & tolerances; regulators; cylinder changeover; expiry control | R | Yes | Yes | Yes | Yes
23 | QAL2 Plan (EN 14181) — Parallel SRM Tests | Calibration / QA | EN sites | Reference methods: EN 14792 (NOx), EN 14791 (SO₂), ISO 12039/EN 15058 (CO/CO₂), O₂ SRM; regression approach; uncertainty target | R | If applicable | If applicable | If applicable | Yes
24 | QAL3 Plan (EN 14181) — Ongoing QA | Calibration / QA | EN sites | Control charts, drift checks, alarm thresholds, maintenance | R | If applicable | If applicable | If applicable | Yes
25 | US EPA RATA/Certification Plan (40 CFR Pt 60/75) | Calibration / QA | US sites | PS-2 (SO₂/NOx), PS-3 (O₂/CO₂), PS-4 (CO); 7-day drift; bias/linearity tests | R | If applicable | If applicable | If applicable | Yes
26 | Power Distribution, Load List & UPS Autonomy | Electrical / Installation | All | Heated lines/probes, analyzers, coolers, DAHS, HVAC/pressurization if in shelter | R | Yes | Yes | Yes | Yes
27 | Wiring Diagrams & Terminal Schedules | Electrical / Installation | All | Analyzer panels, junction boxes, interlocks | R | Yes | Yes | Yes | Yes
28 | Earthing, Bonding & Shielding Scheme | Electrical / Installation | All | Noise control, equipotential bonding, surge arrestors | R | Yes | Yes | Yes | Yes
29 | Hazardous Area Compliance & Certificates (ATEX/IECEx) | Electrical / Installation | Ex installations | Analyzer/probe/heated line/purge panels marking; install conditions | R/F | If applicable | If applicable | If applicable | Yes
30 | Ingress Protection (IP/NEMA) Declarations | Electrical / Installation | Enclosures | IEC 60529/NEMA rating evidence | F | Yes | Yes | Yes | Yes
31 | DAHS Architecture & Data Flow | DAHS / Software | All | Data acquisition, averaging, timebase, alarms, audits, reporting, backups | R | Yes | Yes | Yes | Yes
32 | Regulatory Reporting Configuration | DAHS / Software | All | Averaging periods, substitution rules, outlier handling, hourly/24h reports, emissions units, normalization (O₂/reference conditions) | R | Yes | Yes | Yes | Yes
33 | Communication Protocols & Tag Map (OPC/Modbus) | DAHS / Software | All | Variables (gas conc., diluent, status/QA flags), scaling & units | R/F | Yes | Yes | Yes | Yes
34 | User Management, Cybersecurity & Patch Plan | DAHS / Software | All | Accounts/roles, hardening, AV/allowlisting, patch/test/rollback | R | Yes | Yes | Yes | Yes
35 | Backup/Restore & Disaster Recovery Procedure | DAHS / Software | All | Database backups, archives, periodic export, validation of restores | R | Yes | If applicable | Yes | Yes
36 | FAT Procedure — CEMS | Procedures & FAT | All | Linearity, response time, interference, converter efficiency (NOx), flow checks, alarm & DAHS tests | R/W | Yes | If applicable | Yes | Yes
37 | Start-up, Calibration & Functional Test Procedure (SAT) | Procedures & FAT | All | On-site validation, alarm/inhibit handling, DAHS report verification | R/W | Yes | If applicable | Yes | Yes
38 | Calibration Gas Handling & Safety Procedure | Procedures & FAT | All | Cylinder storage, regulators, purge/vent, leak checks | R | Yes | If applicable | Yes | Yes
39 | EMC/EMI Compliance (IEC 61326) | Compliance Certificates | All | Industrial environment | F | Yes | Yes | Yes | Yes
40 | Electrical Safety (IEC 61010-1) Declaration | Compliance Certificates | All | Safety of electrical equipment | F | Yes | Yes | Yes | Yes
41 | QAL1 Certificates (EN 15267) — copies | Compliance Certificates | EN sites | Provide manufacturer certificates | F | If applicable | If applicable | If applicable | Yes
42 | US EPA Compliance Declarations (if applicable) | Compliance Certificates | US sites | Part 60/75 applicability and PS reference | F | If applicable | If applicable | If applicable | Yes
43 | FAT Test Report — CEMS | Inspection & Test Records | All | Linearity, response time, interference, converter efficiency data, alarms & DAHS results | F/W | Yes | No | Yes | Yes
44 | QAL2 Report (EN 14181) — SRM Correlation | Inspection & Test Records | EN sites | Regression/validation, uncertainty statement | F | If applicable | If applicable | If applicable | Yes
45 | QAL3 Records — Control Charts | Inspection & Test Records | EN sites | Daily/weekly checks, drift trends, alarms | F | If applicable | If applicable | If applicable | Yes
46 | US EPA Certification & RATA Results | Inspection & Test Records | US sites | Relative Accuracy Test Audit data; 7-day drift & linearity | F | If applicable | If applicable | If applicable | Yes
47 | Calibration/Validation Gas Certificates (ISO/IEC 17025) | Inspection & Test Records | All | Blend tolerances, expiry, lot/batch numbers | F | Yes | No | Yes | Yes
48 | Gauge & Calibrator Certificates used | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
49 | Installation, Operation & Maintenance (IOM) Manuals — Analyzer, Sample System, DAHS | Manuals & Installation | All | Install, start-up, maintenance, troubleshooting | F | Yes | No | Yes | Yes
50 | Wiring Diagrams, Loop/Logic Narratives & Interlocks | Manuals & Installation | All | Alarms, inhibits, auto-cal/auto-val routines | F | Yes | No | Yes | Yes
51 | Storage & Handling Instructions | Manuals & Installation | All | Heated components, calibration gases, filters | F | Yes | No | Yes | Yes
52 | As-built Drawings — GA/Sample/Heated Lines/Electrical | As-built & Close-out | All | PDF + native files | F | Yes | No | Yes | Yes
53 | As-built Configuration & Parameter List (per analyzer) | As-built & Close-out | All | Ranges, averaging, alarms, DAHS report setup, comm addresses | F | Yes | No | Yes | Yes
54 | Serial Number-to-Tag/Equipment Cross-Reference | As-built & Close-out | All | Analyzers, probes, heated lines, DAHS servers/PCs with firmware/SW versions | F | Yes | No | Yes | Yes
55 | Recommended Spare Parts List & Maintenance Plan | As-built & Close-out | All | Filters, pumps, lamps, converters, sensors; intervals | F | Yes | No | Yes | Yes
56 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files | F | Yes | No | Yes | Yes
57 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
58 | Preservation & Packing Records with Photos | Packing & Logistics | All | Heated components protection; shock/tilt indicators if specified | F | Yes | No | Yes | Yes
59 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, storage, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — CEMS (CO₂ / CO / NOx / SO₂ / O₂) VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the scope/jurisdiction requires (e.g., EN 14181 QAL2/QAL3 or US EPA Part 60/75 certification).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: CEMS architecture, analyzer principles & ranges, QAL1 certificates, sample probe & heated line details, conditioning P&ID, cross-interference assessment, DAHS reporting setup, power/UPS, wiring/earthing, compliance matrix, and EMC/Electrical/IP declarations.
4) Standards reference (typical): EN 14181 (QAL2/QAL3), EN 15267 (QAL1), EN 15259 (measurement sections), ISO 12039/EN 15058 (CO/CO₂), EN 14792 (NOx), EN 14791 (SO₂); US EPA 40 CFR Part 60/75 PS-2/3/4 where applicable; IEC 61326 (EMC), IEC 61010-1 (safety), IEC 60529 (IP).
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/calcs/procedures — 3–5 weeks; FAT/iFAT procedures — 4 weeks; Final records — prior to shipment.
6) MRB content should include: FAT performance test report, QAL2/QAL3 (or RATA) results as applicable, calibration/validation gas certificates, compliance declarations (EMC/IP/Ex), manuals, as-built drawings & configuration, and packing records.
Notes: If stack flow and dust/opacity monitoring are in scope, include standards EN ISO 16911 (flow) and EN 13284-1 or opacity monitor certification, as separate VDR line items.