## Control Valve VDR
Vendor Document Requirement (VDR) — Control Valve — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Aligned with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. witness/hold points | Project Admin & Planning | All | Hydrostatic, seat leakage, functional/characterization, electrical/Ex checks, painting, packing | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and document submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Valve Datasheet — Control Valve (per tag) | Design & Engineering | All | Type (globe/segment/ball/butterfly), size, rating, end connection, body/trim materials, packing type | R | Yes | Yes | Yes | Yes
7 | Sizing Calculation (Cv/Kv) & Trim Selection | Design & Engineering | All | IEC 60534-2/8 or ISA sizing; FL/xt; rangeability; cavitation/choking/noise checks; anti-cavitation/low-noise trim selection | R | Yes | Yes | Yes | Yes
8 | Flow Characteristic & Rangeability Statement | Design & Engineering | All | Equal %, linear, or modified; inherent vs installed characteristic; required rangeability | R | Yes | Yes | Yes | Yes
9 | Noise Prediction & Mitigation Plan | Design & Engineering | If required | IEC 60534-8 (liquid/gas); predicted dBA; trim/insulation/silencer as required | R | If applicable | If applicable | If applicable | Yes
10 | Anti-cavitation / Erosion Assessment | Design & Engineering | Liquid service | σ/FL criteria; trim/velocity limits; materials upgrade as needed | R | If applicable | If applicable | If applicable | Yes
11 | Actuator Sizing Calculation & Selection | Design & Engineering | All | Breakaway/run/seating forces/torques vs ΔP; supply min/max; safety factor; fail action (FO/FC/FL) | R | Yes | Yes | Yes | Yes
12 | Positioner/Controller Selection & Configuration | Design & Engineering | If smart positioner | Input/output, split-range, characterization, diagnostics (NE107), air set; mounting to IEC 60534-6/VDI/VDE 3845 | R | If applicable | If applicable | If applicable | Yes
13 | Valve–Actuator–Positioner Assembly GA (topworks) | Design & Engineering | All | ISO 5211/IEC interfaces, brackets/couplings, handwheel, travel stops, orientation | R | Yes | Yes | Yes | Yes
14 | Hook-up P&ID / Pneumatic/Electric Schematic | Design & Engineering | All | SOV(s), boosters, quick exhaust, AFR, volume tank, IP65/Ex wiring, earthing | R | Yes | Yes | Yes | Yes
15 | Instrument Wiring Diagram & Terminal Schedule | Design & Engineering | All with instruments | Positioner, SOV, limit switches, feedback transmitters; terminal ident; cable entries | R | Yes | Yes | Yes | Yes
16 | Bill of Materials (Valve + Actuator + Accessories) | Design & Engineering | All | Body/trim, actuator, positioner, SOVs, AFR, boosters, filters, fittings/tubing, feedbacks | R | Yes | Yes | Yes | Yes
17 | Pressure/Temperature Rating Charts & Seat Material Limits | Design & Engineering | All | ASME B16.34; seat/seal temp/DP limits; shaft/seal limits for rotary | R | Yes | Yes | Yes | Yes
18 | Packing/Seal & Fugitive Emissions Plan | Design & Engineering | If FE required | ISO 15848/API 641 class; packing selection and test evidence | R | If applicable | If applicable | If applicable | Yes
19 | Sour Service Compliance Plan | Design & Engineering | If sour service | NACE MR0175/ISO 15156 for wetted parts/fasteners; hardness control | R | If applicable | If applicable | If applicable | Yes
20 | Compliance Matrix to Project Specifications | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
21 | Painting/Coating System & Color Code | Design & Engineering | If painting/coating | System, surface prep class, DFT targets | R | If applicable | If applicable | If applicable | Yes
22 | Hydrostatic Test Procedure (Body) | Procedures & QC | All | API 598 / ISO 5208; test pressure & duration; acceptance | R/W | Yes | If requested | Yes | Yes
23 | Seat Leakage Test Procedure | Procedures & QC | All | ANSI/FCI 70-2 class II–VI; gas/liquid method | R/W | Yes | If requested | Yes | Yes
24 | Functional & Characterization Test Procedure | Procedures & QC | All | Stroke time, hysteresis, deadband, linearity, rangeability; step response; bench set | R/W | Yes | If requested | Yes | Yes
25 | Positioner Calibration & Diagnostics Procedure | Procedures & QC | If smart positioner | Auto-tune, signature, alerts (NE107), PST if configured | R | If applicable | If applicable | If applicable | Yes
26 | Electrical/Ex Verification Procedure | Procedures & QC | If Ex/electric | Enclosure/IP, insulation resistance, earthing, marking | R | If applicable | If applicable | If applicable | Yes
27 | Painting/Coating Procedure & DFT Plan | Procedures & QC | If painting/coating | Surface prep, DFT gauges, holiday test (if specified) | R | If applicable | If applicable | If applicable | Yes
28 | PMI Procedure for Alloy Verification | Procedures & QC | If specified | Define items to verify & acceptance | R | If applicable | If applicable | If applicable | Yes
29 | WPS/PQR/WPQR — Welded Ends/Bodies | Procedures & QC | If welded items | Procedure & welder qualifications | R | If applicable | If applicable | If applicable | Yes
30 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | End caps/flange protectors, desiccants, positioner protections, anti-corrosion measures | R | Yes | No | Yes | Yes
31 | Design Compliance Statement — ASME B16.34 / Body Standard | Compliance & Certifications | All | Body rating & materials | F | Yes | Yes | Yes | Yes
32 | Testing Compliance — API 598 / ISO 5208 | Compliance & Certifications | All | Pressure & seat tests | F | Yes | Yes | Yes | Yes
33 | Fugitive Emissions Certificate | Compliance & Certifications | If required | ISO 15848 / API 641 | F | If applicable | If applicable | If applicable | Yes
34 | ATEX/IECEx Certificates + Schedules (positioner/SOV/limits) | Compliance & Certifications | If Ex devices | Entity parameters, temp class, EPL/Zone, installation conditions | R/F | If applicable | If applicable | If applicable | Yes
35 | EMC/EMI Compliance (IEC 61326) — Positioner/Smart Devices | Compliance & Certifications | If smart device fitted | Industrial environment | F | If applicable | If applicable | If applicable | Yes
36 | Ingress Protection (IEC 60529) Compliance Statement | Compliance & Certifications | Enclosures/monitor boxes | IP rating achieved | F | If applicable | If applicable | If applicable | Yes
37 | PED/CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | Pressure equipment category/module or SEP | F | If applicable | If applicable | If applicable | Yes
38 | NACE MR0175/ISO 15156 Compliance (wetted metallics) | Compliance & Certifications | If sour service | Body/trim/bolting/fasteners (wetted) | F | If applicable | If applicable | If applicable | Yes
39 | Functional Safety (IEC 61508) — Safety Manual & Certificate | Compliance & Certifications | If used in SIS | FMEDA data, proof-test, restrictions | R/F | If applicable | If applicable | If applicable | Yes
40 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | If applicable | If applicable | Yes
41 | Mill Test Certificates (EN 10204 3.1) — pressure containing/wetted parts | Materials & Special Service | All | Body, bonnet, trim, stem/shaft, seat retainers, pressure boundary fasteners | F | Yes | If applicable | Yes | Yes
42 | Elastomer/Polymer Certificates (Seats/Seals/O-rings) | Materials & Special Service | If specified | Material grade & limits; FDA/WRAS if hygienic | F | If applicable | If applicable | If applicable | Yes
43 | Hardness/Impact (Charpy) Reports | Materials & Special Service | If LTCS/low temp or per spec | Per material spec and MDMT | F | If applicable | If applicable | If applicable | Yes
44 | Hydrostatic Test Certificate — Body | Inspection & Test Records | All | Pressure, duration, acceptance | F/W | Yes | No | Yes | Yes
45 | Seat Leakage Test Report — FCI 70-2 Class | Inspection & Test Records | All | Medium, class achieved | F/W | Yes | No | Yes | Yes
46 | Functional & Characterization Test Report | Inspection & Test Records | All | Hysteresis, deadband, linearity, step response; stroking times; fail action | F | Yes | No | Yes | Yes
47 | Positioner Calibration Certificate & Diagnostics | Inspection & Test Records | If smart positioner | Signature, tuning, alerts, PST (if used) | F | If applicable | If applicable | If applicable | Yes
48 | NDE Reports — Welded Ends/Body (RT/UT/MT/PT) | Inspection & Test Records | If welded items | Coverage and results | F | If applicable | If applicable | If applicable | Yes
49 | PMI Reports — Alloy Verification | Inspection & Test Records | If specified | Items verified & results | F | If applicable | If applicable | If applicable | Yes
50 | Painting/Coating DFT & Holiday Test Reports | Inspection & Test Records | If painted/coated | Measured DFT; holiday test results if specified | F | If applicable | If applicable | If applicable | Yes
51 | Dimensional Inspection Report | Inspection & Test Records | All | Face-to-face, end connection details, ISO 5211 interface, travel limits | F | Yes | No | Yes | Yes
52 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
53 | FAT (Factory Acceptance Test) Procedure & Results | Inspection & Test Records | If specified | Protocol signed by parties; punch-list closure | F | If applicable | If applicable | If applicable | Yes
54 | EDD/DTM/Device Files & Version List — Positioner | Software & Integration | If smart positioner | Provide files and compatibility matrix | F | If applicable | If applicable | If applicable | Yes
55 | Comms Conformance Certificate (HART/FF/PA/Modbus) | Software & Integration | If digital comms | FieldComm Group/PI conformance | R/F | If applicable | If applicable | If applicable | Yes
56 | Variable Map & Scaling — Positioner/Feedback | Software & Integration | If digital comms | Variables, units, status bits, diagnostics | F | If applicable | If applicable | If applicable | Yes
57 | Firmware Revision Report & Release Notes | Software & Integration | If smart device | Firmware per serial; known issues/mitigations | F | If applicable | If applicable | If applicable | Yes
58 | Host System Integration Notes | Software & Integration | All | DCS/AMS/PRM/800xA/FDM compatibility and parameters | F | Yes | No | Yes | Yes
59 | Installation, Operation & Maintenance (IOM) Manual — Valve/Actuator/Positioner | Manuals & Installation | All | Mounting, alignment, bench set, air quality, tuning, proof-test instructions | F | Yes | If requested | Yes | Yes
60 | Hook-up, Lifting/Handling & Storage Instructions | Manuals & Installation | All | Tubing materials/size, venting, lifting points, rigging, storage conditions | F | Yes | If requested | Yes | Yes
61 | Recommended Spare Parts List & Interchangeability | Manuals & Installation | All | Seats, seals, packing, SOV coils, filters, kits | F | Yes | If requested | Yes | Yes
62 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | Body/trim codes, Cv/characteristic, actuator model/bench set, positioner ranges/firmware, accessories list | F | Yes | No | Yes | Yes
63 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include actuator/positioner serials and firmware (if any) | F | Yes | No | Yes | Yes
64 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
65 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
66 | Preservation & Packing Records with Photos | Packing & Logistics | All | End caps/flange protectors; positioner covers; shock/humidity indicators if specified | F | Yes | No | Yes | Yes
67 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, lifting/rigging, storage conditions, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Control Valve VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., Ex area, sour service, smart positioner, welded ends, painting).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Datasheet; IEC/ISA sizing with Cv/FL/xt; flow characteristic & rangeability; actuator sizing; assembly GA; hook-up & wiring; materials & rating; compliance matrix; and FE/NACE declarations as applicable.
4) Testing references: API 598/ISO 5208 (hydro/seat); FCI 70-2 (seat leakage class); IEC 60534-6-1 (characterization tests); IEC 61326 (EMC for smart devices).
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/calcs/procedures — 3–4 weeks; Final records — prior to shipment.
6) MRB content should include: hydro & seat test reports; characterization results; positioner calibration; NDE/PMI (if applicable); conformance certificates (ASME/API/ISO/Ex/FE/NACE as applicable); materials certificates; manuals; as-built configuration; and packing list.