## ESD Valve VDR
Vendor Document Requirement (VDR) — ESD (Emergency Shut-Down) Valve — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Aligned with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. witness/hold points | Project Admin & Planning | All | Hydrostatic test, seat leak test, functional stroke test, PST (if applicable) | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and document submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Valve Datasheet — ESDV (per tag) | Design & Engineering | All | Type (ball/butterfly/globe), size, rating, end connection, trim, leakage class, fire-safe requirement | R | Yes | Yes | Yes | Yes
7 | Actuator Sizing Calculation & Selection | Design & Engineering | All | Pneumatic/hydraulic/electric; break/run/seat torques vs DP; min supply; safety factor; fail action (FC/FO) | R | Yes | Yes | Yes | Yes
8 | Valve–Actuator Assembly GA Drawing (topworks) | Design & Engineering | All | ISO 5211 interface, couplings, bracket, stem details, stroke stops, spring can size | R | Yes | Yes | Yes | Yes
9 | Pneumatic/Hydraulic Schematic (Hook-up) | Design & Engineering | If pneumatic/hydraulic | SOV(s) architecture (1oo1/1oo2), boosters, quick exhaust, volume tanks, lock-up, FRL, air quality ISO 8573-1 | R | If applicable | Yes | If applicable | Yes
10 | Instrument Wiring Diagram & Terminal Schedule | Design & Engineering | All with instruments | SOV coils, limit switch/monitor, PST device, junction box entries, earthing | R | Yes | Yes | Yes | Yes
11 | Bill of Materials (Valve + Actuator + Accessories) | Design & Engineering | All | Valve body/trim, actuator, SOVs, limit switch box, PST device, boosters, filters/regulators, fittings/tubing | R | Yes | Yes | Yes | Yes
12 | Fire-safe Design Declaration | Design & Engineering | If required | To be certified to API 607 / ISO 10497 / API 6FA | R | If applicable | Yes | If applicable | Yes
13 | Fugitive Emissions Design Declaration | Design & Engineering | If required | ISO 15848 or API 641 class/limits | R | If applicable | Yes | If applicable | Yes
14 | Pressure/Temperature Rating Charts & Seat Material Limits | Design & Engineering | All | ASME B16.34; seat/seal temp limits; DP limits | R | Yes | Yes | Yes | Yes
15 | Material Selection & Sour Service Compliance Plan | Design & Engineering | If sour service | NACE MR0175/ISO 15156 for wetted parts/fasteners | R | If applicable | If applicable | If applicable | Yes
16 | Functional Safety (SIS) Data Sheet | Design & Engineering | If used in SIF | Architecture, SFF/λD, PFDavg assumptions, proof-test interval, safe states | R | If applicable | Yes | If applicable | Yes
17 | Partial Stroke Test (PST) Strategy & Setup | Design & Engineering | If PST required | PST % travel, inhibit conditions, reset, event capture, bypass arrangements | R | If applicable | If applicable | If applicable | Yes
18 | Valve Torque Data vs DP/Temperature | Design & Engineering | All | Break/run/seat/unseat torques; friction factors; safety margin | R | Yes | Yes | Yes | Yes
19 | Hazardous Area Classification & Device Selection | Design & Engineering | If Ex area | IECEx/ATEX marking for SOV/switch/PST; T-class; EPL/Zone | R | If applicable | If applicable | If applicable | Yes
20 | Compliance Matrix to Project Specifications | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
21 | Painting/Coating System & Color Code | Design & Engineering | If painting/coating | System, surface prep class, DFT targets | R | If applicable | If applicable | If applicable | Yes
22 | Flow Coefficient (Cv/C) Data | Design & Engineering | If required by spec | Applicable mainly to throttling/global scope; optional for on-off ESDV | R | If applicable | If applicable | If applicable | Yes
23 | Hydrostatic Test Procedure (Body) | Procedures & QC | All | API 598 / API 6D; test pressure & duration; acceptance criteria | R/W | Yes | If applicable | Yes | Yes
24 | Seat Leakage Test Procedure | Procedures & QC | All | ISO 5208/API 598 leakage class; gas/liquid method | R/W | Yes | If applicable | Yes | Yes
25 | Functional Stroke Test Procedure | Procedures & QC | All | Stroke time, fail action, end positions; proof of closure; PST steps if applicable | R/W | Yes | If applicable | Yes | Yes
26 | SOV / Pneumatic Accessories Test Procedure | Procedures & QC | If pneumatic | Coil checks, response time, leak checks, quick exhaust, lock-up | R | If applicable | If applicable | If applicable | Yes
27 | Electrical/Instrumentation Test Procedure | Procedures & QC | If instruments fitted | Limit switch setting, continuity, IP checks, insulation resistance | R | If applicable | If applicable | If applicable | Yes
28 | Painting/Coating Procedure & DFT Plan | Procedures & QC | If painting/coating | Surface prep, DFT gauges, holiday test (if specified) | R | If applicable | If applicable | If applicable | Yes
29 | PMI Procedure for Alloy Verification | Procedures & QC | If specified | Define items to verify & acceptance | R | If applicable | If applicable | If applicable | Yes
30 | WPS/PQR/WPQR — Welded Ends/Bodies | Procedures & QC | If welded items | Procedure & welder qualifications | R | If applicable | If applicable | If applicable | Yes
31 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | End caps/flange protectors, desiccants, actuator spring lock, anti-corrosion measures | R | Yes | If applicable | Yes | Yes
32 | API 6D / ISO 17292 / API 609 Compliance Statement (as applicable) | Compliance & Certifications | By valve type | Pipeline isolation and design standards | F | Yes | No | Yes | Yes
33 | Fire-safe Certificate | Compliance & Certifications | If required | API 607 / ISO 10497 / API 6FA | F | If applicable | Yes | If applicable | Yes
34 | Fugitive Emissions Certificate | Compliance & Certifications | If required | ISO 15848 / API 641 | F | If applicable | Yes | If applicable | Yes
35 | PED/CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | Pressure accessory category/module or SEP | F | If applicable | If applicable | If applicable | Yes
36 | ATEX/IECEx Certificates + Schedules (SOV/Limit Switch/PST) | Compliance & Certifications | If Ex devices | Entity parameters, temp class, EPL/Zone, installation conditions | R/F | If applicable | If applicable | If applicable | Yes
37 | Ingress Protection (IP66/67) Compliance Statement | Compliance & Certifications | Enclosures/monitor boxes | IEC 60529 | F | If applicable | If applicable | If applicable | Yes
38 | EMC/EMI Compliance (IEC 61326) — PST/Smart Devices | Compliance & Certifications | If smart device fitted | Industrial environment | F | If applicable | If applicable | If applicable | Yes
39 | Functional Safety (IEC 61508) — SIL Certificate & Safety Manual | Compliance & Certifications | If used in SIF | FMEDA report, SFF, failure rates, proof test; Safety Manual | R/F | If applicable | Yes | If applicable | Yes
40 | NACE MR0175/ISO 15156 Compliance (wetted metallics) | Compliance & Certifications | If sour service | Body/trim/bolting/fasteners (wetted) | F | If applicable | If applicable | If applicable | Yes
41 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | If applicable | If applicable | Yes
42 | Mill Test Certificates (EN 10204 3.1) — pressure containing/wetted parts | Materials & Special Service | All | Body, ball/disc, stem, seat retainers, bonnet, pressure boundary fasteners | F | Yes | No | Yes | Yes
43 | Elastomer/Polymer Certificates (Seats/Seals/O-rings) | Materials & Special Service | If specified | Material grade & limits; FDA/WRAS if hygienic | F | If applicable | No | If applicable | Yes
44 | Impact Test (Charpy) Reports | Materials & Special Service | If LTCS/low temp | Per material spec and MDMT | F | If applicable | No | If applicable | Yes
45 | Hydrostatic Test Certificate — Body | Inspection & Test Records | All | Pressure, duration, acceptance per API 598/6D | F/W | Yes | No | Yes | Yes
46 | Seat Leakage Test Report | Inspection & Test Records | All | Leakage class & medium; acceptance met | F/W | Yes | No | Yes | Yes
47 | Functional Stroke Test Report | Inspection & Test Records | All | Stroke times, fail action, end positions, proof of closure | F | Yes | No | Yes | Yes
48 | PST Baseline & Event Reports | Inspection & Test Records | If PST used | Baseline %, time, diagnostics; success/failure records | F | If applicable | No | If applicable | Yes
49 | Actuator Performance Test Report | Inspection & Test Records | All | Air/hydraulic pressure used; torque output vs required; margins | F | Yes | No | Yes | Yes
50 | SOV/Accessories Functional & Leak Test Records | Inspection & Test Records | If pneumatic | Coil/response/leak tests; booster/quick exhaust checks | F | If applicable | No | If applicable | Yes
51 | NDE Reports — Welded Ends/Body (RT/UT/MT/PT) | Inspection & Test Records | If welded items | Coverage and results | F | If applicable | No | If applicable | Yes
52 | PMI Reports — Alloy Verification | Inspection & Test Records | If specified | Items verified & results | F | If applicable | No | If applicable | Yes
53 | Painting/Coating DFT & Holiday Test Reports | Inspection & Test Records | If painted/coated | Measured DFT; holiday test results if specified | F | If applicable | No | If applicable | Yes
54 | Dimensional Inspection Report | Inspection & Test Records | All | Face-to-face, end connection details, ISO 5211 interface, stem/packing details | F | Yes | No | Yes | Yes
55 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
56 | FAT (Factory Acceptance Test) Procedure & Results | Inspection & Test Records | If specified | Protocol signed by parties; punch-list closure | F | If applicable | No | If applicable | Yes
57 | EDD/DTM/Device Files & Version List — PST/Monitors | Software & Integration | If smart device | Provide files and compatibility matrix | F | If applicable | If applicable | If applicable | Yes
58 | Comms Conformance Certificate (HART/FF/PA/Modbus) | Software & Integration | If digital comms | FieldComm Group/PI conformance | R/F | If applicable | If applicable | If applicable | Yes
59 | Variable Map & Scaling — PST/Monitor | Software & Integration | If digital comms | Variables, units, status bits, diagnostics | F | If applicable | If applicable | If applicable | Yes
60 | Firmware Revision Report & Release Notes | Software & Integration | If smart device | Firmware per serial; known issues/mitigations | F | If applicable | If applicable | If applicable | Yes
61 | Installation, Operation & Maintenance (IOM) Manual — Valve/Actuator/Accessories | Manuals & Installation | All | Mounting, alignment, tubing, electrical, stroke adjust, PST setup, proof-test instructions | F | Yes | No | Yes | Yes
62 | Hook-up & Lifting/Handling Instructions | Manuals & Installation | All | Air set/tubing materials/size, venting, lifting points, rigging, storage | F | Yes | If requested | Yes | Yes
63 | Recommended Spare Parts List & Interchangeability | Manuals & Installation | All | Seats, seals, packing, SOV coils, filters, kits | F | Yes | If requested | Yes | Yes
64 | Storage & Preservation Instructions | Manuals & Installation | All | Actuator spring care, desiccants, periodic stroking | F | Yes | No | Yes | Yes
65 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | Valve model/trim, actuator model, supply set, SOV model, PST settings/disable state, stroke times | F | Yes | No | Yes | Yes
66 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include actuator/monitor/PST serials and firmware (if any) | F | Yes | No | Yes | Yes
67 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
68 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
69 | Preservation & Packing Records with Photos | Packing & Logistics | All | End caps/flange protectors, actuator & topworks protected; shock/humidity indicators if specified | F | Yes | No | Yes | Yes
70 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, lifting/rigging, storage conditions, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — ESD Valve VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., Ex area, sour service, PST, welded ends, painting).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Datasheet, Actuator sizing, Assembly GA, Hook-up & wiring, BOM, P/T rating & torque data, Fire-safe/Fugitive Emissions declarations (if required), Functional-safety summary (if SIS), and Compliance matrix.
4) Standards reference (typical): API 6D / ISO 17292 / API 609; ASME B16.34/16.5/16.25; API 598/ISO 5208 (testing); API 607/6FA/ISO 10497 (fire-safe); ISO 15848/API 641 (FE); IEC 61508 (SIL); IEC 61326 (EMC); IEC 60529 (IP); ISO 8573-1 (instrument air).
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/calcs/procedures — 3–4 weeks; Final records — prior to shipment.
6) MRB content should include: hydrostatic & seat test reports, functional stroke report (and PST reports if used), NDE/PMI results (if applicable), conformance certificates (fire-safe/FE/ATEX/PED/SIL as applicable), materials certificates, manuals, as-built configuration, and packing list.