## ICSS_ICCS VDR
Vendor Document Requirement (VDR) — Complete Control System (ICSS/ICCS) — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Admin & Governance | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Admin & Governance | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP): FAT / iFAT / SAT, witness & hold points | Admin & Governance | All | Define scope, coverage, acceptance criteria | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly / Software Build Schedule | Admin & Governance | All | Milestones and submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Admin & Governance | All |  | R | Yes | No | Yes | No
6 | Configuration & Version Control Plan | Admin & Governance | All | Repository, baselining, change control, backups | R | Yes | No | Yes | No
7 | OT Cybersecurity Management Plan (IEC 62443) | Admin & Governance | All | Hardening, accounts, patching, AV/whitelisting, USB control, remote access | R | Yes | No | Yes | No
8 | Overall ICSS Architecture Diagram | System Architecture & Hardware | All | DCS, SIS/IPS, F&G, Historians, Engineering/HMI, interfaces | R | Yes | Yes | Yes | Yes
9 | Capacity & Sizing Summary | System Architecture & Hardware | All | Controllers, I/O, servers/VMs, clients, licenses; margins & spares policy | R | Yes | Yes | Yes | Yes
10 | Redundancy Architecture (Controllers/Networks/Power) | System Architecture & Hardware | All | Hot/cold standby, switchover, diagnostics | R | Yes | Yes | Yes | Yes
11 | Hardware Platform Bill of Materials (per system & cabinet) | System Architecture & Hardware | All | Part numbers, grades, firmware/hardware revisions | R | Yes | Yes | Yes | Yes
12 | Cabinet GA Drawings (per cabinet) | System Architecture & Hardware | All | Dimensions, layout, ventilation, gland plates, entries | R | Yes | Yes | Yes | Yes
13 | Power Distribution Schematic & Load List | System Architecture & Hardware | All | UPS feeders, PSUs, MCBs, A/B redundancy, breaker sizing | R | Yes | Yes | Yes | Yes
14 | Heat Dissipation & Ventilation Calculation | System Architecture & Hardware | All | Internal temperature rise, fan/AC selection, ambient assumptions | R | Yes | Yes | Yes | Yes
15 | Earthing & Bonding Scheme | System Architecture & Hardware | All | PE/FE bars, segregation, shield terminations | R | Yes | Yes | Yes | Yes
16 | Server / Virtualization Architecture | System Architecture & Hardware | All | Hypervisor, VM layout, storage/RAID, backups, patch window | R | Yes | Yes | Yes | Yes
17 | Thin Clients / HMI Hardware Specification | System Architecture & Hardware | All | Performance, OS image, environmental ratings | R | Yes | Yes | Yes | Yes
18 | Network Architecture & Addressing Plan | Networks & Cybersecurity | All | IP plan, VLANs, routing, firewall rules, zones/conduits | R | Yes | Yes | Yes | Yes
19 | Switches/Firewalls Models & Configuration Baselines | Networks & Cybersecurity | All | ACLs, NAT, VPN, logging, time sync, backups | R | Yes | No | Yes | Yes
20 | Time Synchronization Architecture (NTP/PTP) | Networks & Cybersecurity | All | GPS clocks, stratum, accuracy per SOE requirements | R | Yes | Yes | Yes | Yes
21 | Remote Access & Jump Server Procedure | Networks & Cybersecurity | If remote access | DMZ, MFA, session recording, vendor access control | R | If applicable | If applicable | If applicable | Yes
22 | Ports & Services Whitelist | Networks & Cybersecurity | All | Per node role; change control | R | Yes | Yes | Yes | Yes
23 | Patch & Anti-virus/Allowlisting Plan | Networks & Cybersecurity | All | Schedule, testing, rollback, signature updates | R | Yes | Yes | Yes | Yes
24 | Backup/Restore & Disaster Recovery Procedure | Networks & Cybersecurity | All | Media, frequency, retention, restoration test | R | Yes | Yes | Yes | Yes
25 | I/O Assignment & Count Summary (per subsystem) | I/O & Field Interfaces | All | AI/AO/DI/DO; spares; HART/Fieldbus ports | R | Yes | Yes | Yes | Yes
26 | Instrument Index & Tag Cross-Reference | I/O & Field Interfaces | All | Bidirectional sync rules with owner index | R | Yes | Yes | Yes | Yes
27 | Terminal Wiring Diagrams / Schematic (by cabinet) | I/O & Field Interfaces | All | Marshalling, barriers/isolators, interposing relays | R | Yes | Yes | Yes | Yes
28 | Hook-up Diagrams (signal types) | I/O & Field Interfaces | All | AI/AO/DI/DO, HART, pulse, RTD/TC, solenoids | R | Yes | Yes | Yes | Yes
29 | Hazardous Area Interfaces — Barriers/Isolators | I/O & Field Interfaces | If Ex interfaces | ATEX/IECEx entity parameters; FISCO; earthing | R | If applicable | If applicable | If applicable | Yes
30 | Fieldbus (FF H1/Profibus PA) Segment Design & Calculations | I/O & Field Interfaces | If used | Power conditioners, device per segment, lengths, terminators | R | If applicable | If applicable | If applicable | Yes
31 | HART/Device Manager (AMS/PRM) Configuration Plan | I/O & Field Interfaces | If used | Device files (EDD/DTM), audit trail, alert handling | R | If applicable | If applicable | If applicable | Yes
32 | Package PLC/RTU Interface Control Documents (ICDs) | I/O & Field Interfaces | If packages/RTUs | Data maps, comms (Modbus/Profibus/Profinet/EIP), handshake | R | If applicable | If applicable | If applicable | Yes
33 | OPC UA/DA / MQTT / Protocol Mapping & Tag List | I/O & Field Interfaces | If used | Server roles, tag namespace, security mode | R | If applicable | Yes | If applicable | Yes
34 | SOE I/O Assignment & Time Resolution Plan | I/O & Field Interfaces | All | 1–10 ms SOE; sync dependency to NTP/PTP | R | Yes | Yes | Yes | Yes
35 | Control Narratives & Functional Design Specification (FDS) | Applications (Control) | DCS | Unit ops, interlocks, sequences | R | Yes | Yes | Yes | Yes
36 | Graphics/HMI Philosophy & Sample Screens (ISA-101) | Applications (Control) | All | Color rules, navigation, faceplates | R | Yes | Yes | Yes | Yes
37 | Alarm Philosophy & Rationalization | Applications (Control) | All | EEMUA 191 / ISA-18.2; priority/shelving rules | R | Yes | Yes | Yes | Yes
38 | C&E for Process Interlocks (non-SIS) | Applications (Control) | DCS | Matrix & logic diagrams | R | If applicable | If applicable | If applicable | Yes
39 | Batch/Sequence Design (ISA-88) | Applications (Control) | If batch | Recipes, phases, units, transitions | R | If applicable | If applicable | If applicable | Yes
40 | Historian & Reporting Design | Applications (Control) | All | Tag list, collection rates, compression, retention, reports | R | Yes | Yes | Yes | Yes
41 | SOE & Trending Configuration Strategy | Applications (Control) | All | Resolution, buffering, storage | R | Yes | Yes | Yes | Yes
42 | Naming/Tagging Conventions & Libraries | Applications (Control) | All | Class-based objects, templates, code style | R | Yes | Yes | Yes | Yes
43 | SIS Safety Requirements Specification (SRS) — Vendor Scope | SIS & F&G | If SIS/IPS | IEC 61511; SIF list, trip settings, proof test intervals | R | If applicable | If applicable | If applicable | Yes
44 | SIS Logic Diagrams / Cause & Effect (C&E) | SIS & F&G | If SIS/IPS | Per SRS; bypass/inhibit philosophy | R | If applicable | If applicable | If applicable | Yes
45 | SIL Verification Calculations & Report | SIS & F&G | If required by contract | PFDavg, SFF, proof test coverage; assumptions | R | If applicable | If applicable | If applicable | Yes
46 | Proof Test Procedures & Intervals | SIS & F&G | SIS/IPS | Per SRS; partial/full; pass/fail criteria | R | If applicable | If applicable | If applicable | Yes
47 | F&G Cause & Effect Matrix, Zoning & Detector Coverage | SIS & F&G | If F&G | NFPA 72 / EN 54; coverage report if specified | R | If applicable | If applicable | If applicable | Yes
48 | Logic Solver SIL Certificate & Safety Manual (IEC 61508) | SIS & F&G | SIS/IPS logic solver | SIL capability & restrictions | R/F | If applicable | If applicable | If applicable | Yes
49 | EMC Compliance Certificates | Compliance & Certifications | All | IEC 61326 / 61000-6-2/-6-4 | F | Yes | Yes | Yes | Yes
50 | Environmental/IP/NEMA Rating Declaration | Compliance & Certifications | All | IEC 60529; IEC 60068 | F | Yes | Yes | Yes | Yes
51 | ATEX/IECEx Certificates — Barriers/Isolators/Interfaces | Compliance & Certifications | Ex interfaces | Entity parameters; installation conditions | R/F | If applicable | If applicable | If applicable | Yes
52 | UL/CSA/CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | DoC listing standards/directives | F | If applicable | If applicable | If applicable | Yes
53 | IEC 61511 Compliance Statement (vendor scope) | Compliance & Certifications | If SIS | Lifecycle responsibilities as per contract | F | If applicable | If applicable | If applicable | Yes
54 | Cybersecurity Conformance (IEC 62443-4-1/-4-2 if applicable) | Compliance & Certifications | All | Supplier process & component conformance | F | If applicable | If applicable | If applicable | Yes
55 | FAT Procedure (DCS/IPS/F&G) | Testing & Validation | All | Coverage, sampling, documentation | R/W | Yes | If requested | Yes | Yes
56 | Integrated FAT (iFAT) Plan | Testing & Validation | If 3rd parties | Interfaces with packages/ESD/PLC/RTU | R/W | If applicable | If applicable | If applicable | Yes
57 | SAT / Pre-commissioning Procedure | Testing & Validation | All | Loop checks, marshalling, cabinet power-up | R/W | Yes | If requested | Yes | Yes
58 | Performance Test Plan — Redundancy/Latency/Throughput | Testing & Validation | All | Switchover, controller loading, network KPIs | R/W | Yes | If requested | Yes | Yes
59 | UPS Autonomy & Power Failover Test Plan | Testing & Validation | If IPS/F&G or UPS | Autonomy verification; logs | R/W | If applicable | If applicable | If applicable | Yes
60 | EMC/Environmental Test Plans (project-specific) | Testing & Validation | If specified | Conducted/radiated; immunity; thermal soak | R/W | If applicable | If applicable | If applicable | Yes
61 | Cybersecurity Factory Configuration Verification | Testing & Validation | All | Baseline scan, hardening checklist, account audit | R/W | Yes | If requested | Yes | Yes
62 | System Backup Images & Configuration Files | Software & Integration | All | Controller/servers/HMIs; restore instructions | F | Yes | No | Yes | Yes
63 | Version List (HW/FW/SW) & Patch Levels | Software & Integration | All | Per cabinet/module/server with serials | F | Yes | No | Yes | Yes
64 | License Keys/Dongles Report | Software & Integration | All | Counts, expiry, media | F | Yes | No | Yes | Yes
65 | OPC/Protocol Servers & Tag Export | Software & Integration | If used | Browseable namespace; access control | F | If applicable | If applicable | If applicable | Yes
66 | IOM Manuals — Controllers/Servers/Networks/Cabinets | Manuals & Training | All | Install, operation, maintenance | F | Yes | No | Yes | Yes
67 | Cybersecurity Hardening Guide (site) | Manuals & Training | All | Accounts, services, firewall rules, whitelisting | F | Yes | No | Yes | Yes
68 | User Account Management SOP | Manuals & Training | All | Roles, privileges, password policy, MFA | F | Yes | No | Yes | Yes
69 | Maintenance & Troubleshooting Manual | Manuals & Training | All | Fault isolation, diagnostics, spares | F | Yes | No | Yes | Yes
70 | Training Plan & Materials (Operator/Maintenance) | Manuals & Training | All | Agendas, handouts, attendance | F | If applicable | If applicable | If applicable | Yes
71 | Recommended Spare Parts List & MTBF Data | Manuals & Training | All | Critical spares, quantities | F | Yes | No | Yes | Yes
72 | As-built Drawings — GA/Wiring/Network/Power | As-built & Close-out | All | PDF + native files | F | Yes | No | Yes | Yes
73 | Final I/O List & Cross-Reference | As-built & Close-out | All | Terminals/channels vs tag list | F | Yes | No | Yes | Yes
74 | Final Configuration Report (modules/controllers/servers) | As-built & Close-out | All | Slots, options, firmware; serials | F | Yes | No | Yes | Yes
75 | Serial Number-to-Tag/Cabinet Cross-Reference | As-built & Close-out | All | Include firmware versions | F | Yes | No | Yes | Yes
76 | Warranty Certificates | As-built & Close-out | All | Coverage & start date | F | Yes | No | Yes | Yes
77 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + media | F | Yes | No | Yes | Yes
78 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
79 | Pre-delivery Inspection (PDI) Checklist & Photos | Pre-delivery & Logistics | All | Internal photos, labels, wiring tidiness | F | Yes | No | Yes | Yes
80 | Preservation & Packing Records with Photos | Pre-delivery & Logistics | All | Desiccants, tilt/shock indicators, rack protections | F | Yes | No | Yes | Yes
81 | Shipping & Handling Instructions | Pre-delivery & Logistics | All | Lifting/handling, storage, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Complete Control System (ICSS/ICCS) VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the scope requires (e.g., SIS/F&G in scope, Ex interfaces, batch, packages/RTUs).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: ICSS architecture, capacity & redundancy, network plan, cabinet GA, I/O/spares policy, naming/graphics/alarm philosophies, historian/reporting design, compliance declarations (EMC/IP) and cybersecurity plan; SIS/F&G items if included in scope.
4) Standards reference (typical): IEC 61511/61508 (SIS lifecycle & logic solver), NFPA 72/EN 54 (F&G), IEC 62443 (OT cybersecurity), IEC 61326/61000-6-x (EMC), IEC 60529/60068 (IP/env), ISA-18.2 & EEMUA 191 (alarm), ISA-101 (HMI), ISA-88 (batch).
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Architecture/drawings/calcs — 3–5 weeks; FAT/iFAT procedures — 4 weeks; Final records — prior to shipment.
6) MRB content should include: FAT/iFAT/SAT & performance test reports, conformance certificates (EMC/IP/Ex/SIL as applicable), backup images & version lists, licenses, manuals & cybersecurity guides, as-built drawings/I/O lists, PDI photos, and packing list.