## PD Flowmeter VDR
Vendor Document Requirement (VDR) — Positive Displacement (PD) Flowmeter — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. calibration/proving, witness points | Project Admin & Planning | All | Include water-draw/master meter proving, pressure/leak test, electronics checks | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and document submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Instrument Datasheet — PD Flowmeter (per tag) | Design & Engineering | All | Meter type (oval/helical/rotary/nutating), size, range, viscosity/temperature range, pressure class, outputs, Ex rating | R | Yes | Yes | Yes | Yes
7 | Application & Sizing Check | Design & Engineering | All | Viscosity window, turndown, differential pressure/backpressure, pulsation/air entrainment, filtering & strainer mesh, required minimum backpressure | R | Yes | Yes | Yes | Yes
8 | Accuracy, Linearity & Repeatability Statement | Design & Engineering | All | Base accuracy; linearity across flow & viscosity; repeatability; temp/visc effects | R | Yes | Yes | Yes | Yes
9 | Pressure Loss (ΔP) vs Flow & Viscosity Curves | Design & Engineering | All | Include multiple viscosities; cavitation/backpressure notes | R | Yes | Yes | Yes | Yes
10 | General Arrangement (GA) Drawing — Meter Body & Pickoff | Design & Engineering | All | Face-to-face, end connections, rotor/gear chamber outline, pickoff sensor, junction box | R | Yes | Yes | Yes | Yes
11 | Materials of Construction (wetted & non-wetted) | Design & Engineering | All | Body, rotors/gears, shafts, bearings, seals/elastomers, magnets/couplings, fasteners | R | Yes | Yes | Yes | Yes
12 | Temperature & Pressure Limits / Derating | Design & Engineering | All | Allowable service envelope; seal/seat/elastomer temp limits | R | Yes | Yes | Yes | Yes
13 | Air/Gas Entrapment & Pulsation Mitigation Plan | Design & Engineering | All | Air eliminators/degassers, pulsation dampeners, installation orientation | R | Yes | Yes | Yes | Yes
14 | Viscosity/Temperature Compensation Strategy | Design & Engineering | If compensation used | Algorithm; RTD input; live K-factor correction; fluid coefficients | R | If applicable | If applicable | If applicable | Yes
15 | Compliance Matrix to Project Specs / Datasheet | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
16 | Bypass/Isolation & Strainer/Filter Arrangement Drawing | Design & Engineering | All | Recommended line arrangement; strainer mesh; air eliminator; proving ports | R | Yes | Yes | Yes | Yes
17 | Calibration / Proving Procedure | Procedures & QC | All | Water draw or master meter; base conditions; uncertainty budget; K-factor computation; multiple viscosities & flow points | R/W | Yes | If requested | Yes | Yes
18 | Functional Test Procedure — Outputs & Totalizers | Procedures & QC | All | Pulse output (open collector/reed), 4–20 mA/HART, direction detection, cutoff settings, NE43/NE107 | R | Yes | If requested | Yes | Yes
19 | Pressure Test / Leak Test Procedure | Procedures & QC | All | Body shell test; leak test across seals; acceptance criteria | R/W | Yes | If requested | Yes | Yes
20 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | Protection of rotor chamber; caps; moisture barriers; O₂-clean if specified | R | Yes | No | Yes | Yes
21 | Painting/Coating Procedure & DFT Plan | Procedures & QC | If painted/coated | System, surface prep, DFT gauges & hold points | R | If applicable | If applicable | If applicable | Yes
22 | PMI Procedure for Alloy Verification | Procedures & QC | If specified | Define items to verify & acceptance | R | If applicable | If applicable | If applicable | Yes
23 | Custody Transfer / Legal Metrology Declaration | Compliance & Certifications | If fiscal service | OIML R117 / MID MI-005 / API MPMS Ch. 5.5; model approval if applicable | R/F | If applicable | If applicable | If applicable | Yes
24 | Calibration Lab Accreditation | Compliance & Certifications | If fiscal certs required | ISO/IEC 17025 lab accreditation for prover/water draw | F | If applicable | If applicable | If applicable | Yes
25 | EMC/EMI Compliance Statement (IEC 61326) | Compliance & Certifications | All with electronics | Industrial environment | F | Yes | Yes | Yes | Yes
26 | Electrical Safety (IEC 61010-1) Declaration | Compliance & Certifications | All with electronics | Safety of electrical equipment | F | Yes | Yes | Yes | Yes
27 | Ingress Protection (IP66/67) Compliance Statement | Compliance & Certifications | Electronics enclosure | IEC 60529 | F | Yes | Yes | Yes | Yes
28 | ATEX/IECEx Certificates + Schedules | Compliance & Certifications | If Ex area | Entity parameters, temp class, EPL/Zone, install conditions | R/F | If applicable | If applicable | If applicable | Yes
29 | PED/CE/UKCA Declaration (as applicable) | Compliance & Certifications | Pressure accessory | Category/Module or SEP | F | If applicable | If applicable | If applicable | Yes
30 | NACE MR0175/ISO 15156 Compliance (wetted metallics) | Compliance & Certifications | If sour service | Body/rotor/fasteners (wetted) | F | If applicable | If applicable | If applicable | Yes
31 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | If applicable | If applicable | Yes
32 | Mill Test Certificates (EN 10204 3.1) — wetted metallics | Materials & Special Service | All wetted metallics | Body, rotors/gears, shafts, chamber, pressure boundary fasteners | F | Yes | If applicable | Yes | Yes
33 | Elastomer/Polymer Compliance (FDA/WRAS if required) | Materials & Special Service | If hygienic or specified | Seals, O-rings approvals | F | If applicable | If applicable | If applicable | Yes
34 | Calibration / Proving Certificate (Meter Factor/K-factor) | Inspection & Test Records | All | K-factor (pulses/unit) at base conditions; meter factor vs flow & viscosity; linearity/repeatability; uncertainty; reference standards used | F/W | Yes | No | Yes | Yes
35 | Viscosity/Temperature Compensation Verification | Inspection & Test Records | If compensation used | Algorithm validation; RTD mapping; corrected vs uncorrected tests | F | If applicable | No | If applicable | Yes
36 | Functional Test Report — Outputs/Totalizers/Direction | Inspection & Test Records | All | Pulse integrity, scaling, cutoff, 4–20 mA/HART, diagnostics | F | Yes | No | Yes | Yes
37 | Pressure Test / Leak Test Certificate | Inspection & Test Records | All | Body shell and leak across seals | F/W | Yes | No | Yes | Yes
38 | Dimensional Inspection Report | Inspection & Test Records | All | Face-to-face, end connections, orientation features | F | Yes | No | Yes | Yes
39 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates; prover/water draw certificates | F | Yes | No | Yes | Yes
40 | Painting/Coating DFT Report | Inspection & Test Records | If painted/coated | DFT readings vs spec | F | If applicable | No | If applicable | Yes
41 | EDD/DTM/Device Files & Version List | Software & Integration | Smart transmitters | Provide files and compatibility matrix | F | If applicable | If applicable | If applicable | Yes
42 | Communication Conformance Certificate (HART/FF/PA/Modbus) | Software & Integration | Digital comms devices | FieldComm Group/PI conformance | R/F | If applicable | If applicable | If applicable | Yes
43 | Modbus/HART Variable Map & Scaling | Software & Integration | If Modbus/HART used | Variables (totalized, flow rate, status), units, scaling, direction bits | F | If applicable | If applicable | If applicable | Yes
44 | Firmware Revision Report & Release Notes | Software & Integration | All smart devices | Device firmware per serial; known issues/mitigations | F | If applicable | If applicable | If applicable | Yes
45 | Host System Integration Notes | Software & Integration | All | DCS/PLC/SCADA integration, pulse integrity, debounce, totalizer rollover | F | Yes | No | Yes | Yes
46 | Installation, Operation & Maintenance (IOM) Manual | Manuals & Installation | All | Orientation, strainers/filters, air elimination, bypass, proving ports, zeroing, maintenance | F | Yes | If requested | Yes | Yes
47 | Wiring Diagrams & Mounting Templates | Manuals & Installation | All | Terminals, entries, clearances, ground/bonding | F | Yes | If requested | Yes | Yes
48 | Storage & Handling Instructions | Manuals & Installation | All | Protect rotor chamber; shipping locks; moisture control | F | Yes | No | Yes | Yes
49 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | K-factor, cutoffs, damping, comm address, compensation settings | F | Yes | No | Yes | Yes
50 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include model code and firmware version | F | Yes | No | Yes | Yes
51 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
52 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
53 | Preservation & Packing Records with Photos | Packing & Logistics | All | Caps, desiccants, rotor locks; shock/humidity indicators if specified | F | Yes | No | Yes | Yes
54 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, handling, storage, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Positive Displacement (PD) Flowmeter VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the scope requires (e.g., Ex area, fiscal custody transfer, sour service, hygienic service, smart transmitter).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Datasheet, Application/viscosity window & turndown check, Accuracy/linearity statement, ΔP vs flow & viscosity curves, GA drawing, Materials list, Service limits, Air/pulsation mitigation plan, Compliance matrix, and EMC/Safety/IP declarations; Ex/fiscal as applicable.
4) Calibration & proving: provide K-factor and meter factor versus flow & viscosity, base conditions, uncertainty budget, and reference standards (water draw or master meter). For fiscal service, include OIML R117/MID/API MPMS 5.5 declarations and 17025 lab evidence.
5) Installation notes: always use strainers/filters and air eliminators as specified; ensure minimum backpressure; consider bypass/isolations for maintenance and proving ports for in-situ verification.
6) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/calcs/procedures — 3–4 weeks; Final records — prior to shipment.
7) MRB content should include: calibration/proving certificate (with K-factor tables), functional & pressure tests, conformance certificates (Ex/IP/EMC/PED/NACE as applicable), materials certificates, manuals, as-built configuration, and packing list.