## Pressure_DP Transmitter VDRL
Vendor Document Requirement List (VDRL) — Pressure / DP Transmitters — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. calibration & witness points | Project Admin & Planning | All | Include bench calibration, leak checks, functional tests | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and submission plan | R | Yes | No | Yes | No
5 | Nonconformance/Concession/Deviation & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Instrument Datasheet — Pressure / DP Transmitter (per tag) | Design & Engineering | All | Model, range limits, output, turndown, materials, tapping/connection | R | Yes | Yes | Yes | Yes
7 | Configuration / Range Sheet (LRV/URV, units, damping, fail-safe) | Design & Engineering | All | Include square-root selection for DP flow, upscale/downscale | R | Yes | Yes | Yes | Yes
8 | Performance & Accuracy Statement | Design & Engineering | All | Total probable error, reference accuracy, stability, temp/static effects | R | Yes | Yes | Yes | Yes
9 | Materials of Construction List (wetted & non-wetted) | Design & Engineering | All | Diaphragm, process flange/seal, fill fluid (if remote seal), manifold | R | Yes | Yes | Yes | Yes
10 | Hook-up / Typical Installation Drawing (vendor proposal) | Design & Engineering | All | Impulse line/tubing sizes, manifold type, drain/vent, mounting | R | Yes | If requested | Yes | Yes
11 | Remote Seal System Design (if applicable) | Design & Engineering | If remote seal/capillary supplied | Capillary length, fill fluid, temp limits, diaphragm material | R | If applicable | If applicable | If applicable | Yes
12 | Manifold Specification (2/3/5-valve) & GA | Design & Engineering | If manifold in scope | Pressure class, materials, mounting, vent/drain, isolation | R | If applicable | If applicable | If applicable | Yes
13 | Compliance Matrix to Project Spec / Datasheet | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
14 | Calibration Procedure (traceable) | Procedures & QC | All | ISO/IEC 17025 traceability; 5-point or as specified | R | Yes | No | Yes | Yes
15 | Functional Test Procedure | Procedures & QC | All | Loop output, fail-safe action, simulation, damping check | R | Yes | No | Yes | Yes
16 | Cleaning & Oxygen Service Procedure | Procedures & QC | If O2/clean service | Oxygen cleaning verification method & acceptance | R | If applicable | If applicable | If applicable | Yes
17 | Leak Test Procedure (seals/manifold) | Procedures & QC | If seals/manifold in scope | Medium, pressure, duration, acceptance criteria | R/W | If applicable | If applicable | If applicable | Yes
18 | Preservation/Packing Procedure | Procedures & QC | All | Shipping caps, environmental controls, shock indicators | R | Yes | No | Yes | Yes
19 | Software/Firmware Handling & Cybersecurity Hardening Guide | Procedures & QC | All smart transmitters | Default passwords, write lock, security switch, OTA policy | R | Yes | No | Yes | Yes
20 | ATEX/IECEx (or regional) Hazardous Area Certificates + Schedules | Compliance & Certifications | If Ex-rated required | Entity parameters, temp class, EPL/Zone, installation conditions | R/F | If applicable | Yes | If applicable | Yes
21 | Functional Safety (IEC 61508) SIL Capability Certificate | Compliance & Certifications | If used in SIS | SIL cap, SFF, PFDavg data, β-factor assumptions; Safety Manual | R/F | If applicable | Yes | If applicable | Yes
22 | Field Communication Conformance Certificate (HART/FF/Profibus PA) | Compliance & Certifications | Digital comms devices | FieldComm Group/PI test report or certificate | R/F | If applicable | Yes | If applicable | Yes
23 | PED/UKCA/CE Declaration (if in scope) | Compliance & Certifications | If jurisdiction requires | Category/Module or SEP as applicable | F | If applicable | If applicable | If applicable | Yes
24 | Ingress Protection (IP) & EMC Compliance Statement | Compliance & Certifications | All | IP66/67 as applicable; EMC per standards list | F | Yes | If requested | Yes | Yes
25 | NACE MR0175/ISO 15156 Compliance (wetted metallics) | Compliance & Certifications | If sour service | All wetted parts & fasteners coverage | F | If applicable | If applicable | If applicable | Yes
26 | Mill Test Certificates (EN 10204 3.1) — wetted components | Materials & Special Service | All wetted metallics | Diaphragm, process flanges/seals, manifolds, fasteners | F | Yes | No | Yes | Yes
27 | Fill Fluid TDS & SDS (remote seal) | Materials & Special Service | If remote seal/capillary | Compatibility, temp range, viscosity, toxicity | F | If applicable | If applicable | If applicable | Yes
28 | Elastomer/Polymer Compliance (FDA/WRAS if required) | Materials & Special Service | If specified | O-rings/gaskets approvals | F | If applicable | If applicable | If applicable | Yes
29 | Calibration Certificate (as-left) | Inspection & Test Records | All | Traceable to ISO/IEC 17025; 5-point ascending/descending | F/W | Yes | No | Yes | Yes
30 | Functional Test Report | Inspection & Test Records | All | Output check, alarm/fail-safe, damping verification | F | Yes | No | Yes | Yes
31 | Leak/Pressure Test Certificate — manifold/seal system | Inspection & Test Records | If manifold/seal in scope | Hydro/pneumatic per procedure | F/W | If applicable | No | If applicable | Yes
32 | Oxygen Service Cleanliness Certificate | Inspection & Test Records | If O2 service | Visual/UV inspection records | F | If applicable | No | If applicable | Yes
33 | Environmental/Temperature Soak Test Record (if specified) | Inspection & Test Records | If contract requires | Hot/cold soak, output stability | F | If applicable | No | If applicable | Yes
34 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
35 | EDD/DTM/Device Files & Version List | Software & Integration | Smart devices | Provide files and version compatibility matrix | F | Yes | If requested | Yes | Yes
36 | GSD/EDS/CFH files (Profibus PA/FF) | Software & Integration | If using FF/PA | Node address defaults, function block info | F | If applicable | If applicable | If applicable | Yes
37 | Host System Integration Notes | Software & Integration | All | DCS/AMS/PRM/800xA/FDM compatibility and parameters | F | Yes | If requested | Yes | Yes
38 | Firmware Revision Report & Release Notes | Software & Integration | All | Device firmware version per serial; issues/mitigations | F | Yes | No | Yes | Yes
39 | Installation, Operation & Maintenance (IOM) Manual | Manuals & Installation | All | Entity parameters, wiring, hazardous area instructions | F | Yes | No | Yes | Yes
40 | Safety Manual (IEC 61508) | Manuals & Installation | If used in SIS | Proof test intervals, failure rates, restrictions | F | If applicable | If applicable | If applicable | Yes
41 | Mounting/Bracket Drawings & Torque Values | Manuals & Installation | All | Includes coplanar/manifold mounting | F | Yes | No | Yes | Yes
42 | Storage & Handling Instructions | Manuals & Installation | All | Caps, humidity/temp storage, seal protection | F | Yes | No | Yes | Yes
43 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | LRV/URV, units, damping, output mode, address | F | Yes | No | Yes | Yes
44 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include year/week code, firmware version | F | Yes | No | Yes | Yes
45 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
46 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
47 | Preservation & Packing Records with Photos | Packing & Logistics | All | Transit shock/humidity indicators if specified | F | Yes | No | Yes | Yes
48 | Shipping, Handling & Lifting Instructions | Packing & Logistics | All | Orientation for capillary/seal assemblies | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Pressure / DP Transmitters
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., SIS use, Ex area, remote seals).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Datasheet, Configuration, Performance statement, Materials list, Compliance matrix, Ex/SIL/Comms certs (as applicable).
4) Standards reference: ISO/IEC 17025 (calibration), IEC 61508 (SIL), IEC 61511 (SIS lifecycle—user ref), IEC 60079 series (hazardous area), FieldComm Group/PI conformance, EN 10204 (MTC), NACE MR0175/ISO 15156 (sour).
5) Suggested initial due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/config docs — 3–4 weeks; Final records — prior to shipment.
6) MRB content should include: calibration certificates, test records, conformance certificates, materials certificates, manuals, as-built configuration, and packing list.