## System Cabinets VDR
Vendor Document Requirement (VDR) — System Cabinets (DCS / IPS / F&G) — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Aligned with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP): FAT/iFAT/SAT, witness & hold points | Project Admin & Planning | All | Define scope, test coverage, sample sizes, acceptance criteria | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly / Software Build Schedule | Project Admin & Planning | All | Milestones and submittal plan | R | Yes | No | Yes | No
5 | Deviation/Concession (NCR) & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Configuration & Version Control Plan | Project Admin & Planning | All | Repository, baselining, change control, backups | R | Yes | No | Yes | No
7 | OT Cybersecurity Management Plan (IEC 62443) | Project Admin & Planning | All | Accounts, hardening, patching, AV/whitelisting, USB control | R | Yes | No | Yes | No
8 | System Architecture Diagram — DCS/IPS/F&G with interfaces | System Architecture & Design | All | Controllers, servers, HMIs, gateways, historians, third-party links | R | Yes | Yes | Yes | Yes
9 | Cabinet GA Drawings (per cabinet) | System Architecture & Design | All | Dimensions, layout, ingress/ventilation, gland plates, cable entries | R | Yes | Yes | Yes | Yes
10 | Power Distribution Schematic & Load List | System Architecture & Design | All | UPS feeders, MCBs, PSUs, redundancy (A/B), breaker sizing | R | Yes | Yes | Yes | Yes
11 | Heat Dissipation & Ventilation Calculation | System Architecture & Design | All | Cabinet internal temperature rise, fans/filters/AC, ambient assumptions | R | Yes | Yes | Yes | Yes
12 | Earthing & Bonding Scheme | System Architecture & Design | All | PE/FE bars, segregation, shield terminations | R | Yes | Yes | Yes | Yes
13 | I/O Assignment & Count Summary (per subsystem) | System Architecture & Design | All | Spare policy; AI/AO/DI/DO; HART/fieldbus ports | R | Yes | Yes | Yes | Yes
14 | Terminal Wiring Diagrams / Schematic (by cabinet) | System Architecture & Design | All | Marshalling, barriers/isolators, interposing relays | R | Yes | No | Yes | Yes
15 | Interface / Hook-up Diagrams — 3rd Party Systems | System Architecture & Design | As applicable | Modbus/Profibus/Profinet/OPC; serial/Ethernet details | R | If applicable | If applicable | If applicable | Yes
16 | Network Architecture & Addressing Plan | System Architecture & Design | All | IP plan, VLANs, routing, firewall rules, zones/conduits | R | Yes | Yes | Yes | Yes
17 | Fiber/Copper Network Drawings & Patch Panel Schedules | System Architecture & Design | All | Splicing, LIUs, redundancy (RSTP/PRP/MRP), media converters | R | Yes | Yes | Yes | Yes
18 | Bill of Materials (per cabinet & system) | System Architecture & Design | All | Part nos., grades, firmware/hardware revisions | R | Yes | Yes | Yes | Yes
19 | Hazardous Area Compliance — Barriers/Isolators | System Architecture & Design | If Ex interfaces | ATEX/IECEx data, entity parameters, FISCO/Ex ia/ib | R | If applicable | If applicable | If applicable | Yes
20 | Environmental Ratings & Derating (IP/NEMA, temp, vibration) | System Architecture & Design | All | IEC 60529, IEC 60068, outdoor cabinet options | R | Yes | Yes | Yes | Yes
21 | Seismic Qualification (if specified) | System Architecture & Design | If required by project | IEC/IEEE 344 or local code | R | If applicable | If applicable | If applicable | Yes
22 | EMC Compliance Plan | System Architecture & Design | All | IEC 61326 / IEC 61000-6-2/-6-4 approach | R | Yes | Yes | Yes | Yes
23 | Compliance Matrix to Project Specs | System Architecture & Design | All | Point-by-point compliance; deviations listed | R | Yes | Yes | Yes | Yes
24 | Software Licensing & Part Numbers Summary | System Architecture & Design | All | Server/engineering/Historian/HMI; seat counts; dongles | R | Yes | Yes | Yes | Yes
25 | DCS Application Design Spec (FBD/SFC/Logic diagrams) | Application & Functional Design | DCS | Control narratives, interlocks, sequences | R | Yes | No | Yes | Yes
26 | IPS/SIS SRS & C&E (IEC 61511) | Application & Functional Design | IPS/SIS | SIF definitions, trip settings, proof test intervals | R | If applicable | If applicable | If applicable | Yes
27 | F&G Cause & Effect Matrix, Zoning & Detector Coverage | Application & Functional Design | F&G | NFPA 72 / EN 54 principles; coverage report if specified | R | If applicable | If applicable | If applicable | Yes
28 | Alarm Philosophy & Rationalization | Application & Functional Design | All | EEMUA 191 / ISA-18.2; priority & shelving rules | R | Yes | Yes | Yes | Yes
29 | HMI/Graphics Philosophy & Sample Screens | Application & Functional Design | All | ISA-101 style guide, color & navigation rules | R | Yes | Yes | Yes | Yes
30 | SOE Strategy & Time Synchronization Architecture | Application & Functional Design | All | 1 ms/10 ms resolution as specified; NTP/PTP; GPS clock | R | Yes | Yes | Yes | Yes
31 | Cable Schedule & Cable Block Diagrams (to/from cabinets) | Application & Functional Design | All | Numbering, terminations, gland type; test requirements | R | Yes | No | Yes | Yes
32 | Terminal Plans & Loop Drawings | Application & Functional Design | All | Per loop/point; barrier/isolator details | R | Yes | No | Yes | Yes
33 | UPS/Battery Autonomy Calculations (IPS/F&G) | Application & Functional Design | IPS/F&G | Required backup time, load profiles, test method | R | If applicable | If applicable | If applicable | Yes
34 | Redundancy Configuration (Controllers/Networks/Power) | Application & Functional Design | All | Hot/cold standby, switchover strategy, diagnostics | R | Yes | Yes | Yes | Yes
35 | FAT Procedure (DCS/IPS/F&G) | Procedures & QC | All | Coverage, sampling, documentation, punch list | R/W | Yes | If requested | Yes | Yes
36 | Integrated FAT (iFAT) Plan | Procedures & QC | If 3rd parties | Interfaces tested with packages/ESD | R/W | If applicable | If applicable | If applicable | Yes
37 | SAT / Pre-commissioning Procedure | Procedures & QC | All | Loop checks, marshalling, panel power-up | R/W | Yes | No | Yes | Yes
38 | Software Test Plan (unit/integration) & Factory Checklists | Procedures & QC | All | Test cases, acceptance, evidence capture | R | Yes | No | Yes | Yes
39 | Backup/Restore & Disaster Recovery Procedure | Procedures & QC | All | Media, frequency, retention, verification | R | Yes | No | Yes | Yes
40 | AV/Whitelisting & Patch Management Procedure | Procedures & QC | All | Schedule, exceptions, testing, rollback | R | Yes | No | Yes | Yes
41 | Obsolescence / Lifecycle Support Plan | Procedures & QC | All | LCS window, spares, upgrade path | R | Yes | No | Yes | Yes
42 | SIL Certificate & Safety Manual — Logic Solver (IEC 61508) | Compliance & Certifications | IPS/F&G logic solver | SIL capability, restrictions, PFDavg assumptions | R/F | If applicable | No | If applicable | Yes
43 | IEC 61511 Compliance Statement (vendor scope) | Compliance & Certifications | IPS/SIS | Lifecycle responsibilities as per contract | F | If applicable | If applicable | If applicable | Yes
44 | EMC Compliance Certificates | Compliance & Certifications | All | IEC 61326 / 61000-6-2/-6-4 | F | Yes | No | Yes | Yes
45 | Environmental/IP/NEMA Rating Declaration | Compliance & Certifications | All | IEC 60529; enclosure class | F | Yes | No | Yes | Yes
46 | ATEX/IECEx Certificates — Barriers/Isolators/Field Interfaces | Compliance & Certifications | Ex interfaces | Entity parameters; installation conditions | R/F | If applicable | If applicable | If applicable | Yes
47 | UL/CSA/CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | DoC listing standards/directives | F | If applicable | If applicable | If applicable | Yes
48 | F&G Panel Approvals/Listing (NFPA 72/EN 54) | Compliance & Certifications | F&G only | Listing or certificate per panel model | F | If applicable | If applicable | If applicable | Yes
49 | Cybersecurity Conformance Statement (IEC 62443-4-1/4-2, if applicable) | Compliance & Certifications | All | Supplier/process and component conformance | F | If applicable | If applicable | If applicable | Yes
50 | Cabinet/Enclosure Certificates of Conformance | Materials & Special | All | Material grade, coating, IP rating CoC | F | Yes | No | Yes | Yes
51 | Cables & Accessories Certificates (if specified) | Materials & Special | If specified | FRLS/LSZH/armoring as per spec | F | If applicable | If applicable | If applicable | Yes
52 | FAT Report with Punch List Closure | Inspection & Test Records | All | Signed by parties; evidence attached | F/W | Yes | No | Yes | Yes
53 | Integrated FAT (iFAT) Report | Inspection & Test Records | If performed | 3rd party packages/interfaces | F/W | If applicable | No | If applicable | Yes
54 | SAT / Pre-commissioning Reports | Inspection & Test Records | All | Loop checks, panel energization | F | Yes | No | Yes | Yes
55 | Network Performance Test Report | Inspection & Test Records | All | Latency, redundancy switchover, packet loss | F | Yes | No | Yes | Yes
56 | Heat Run / Soak Test Report | Inspection & Test Records | All | Thermal stability at load | F | If applicable | If applicable | If applicable | Yes
57 | Power Failover / UPS Autonomy Test Report | Inspection & Test Records | IPS/F&G | Autonomy time achieved; switchover logs | F | If applicable | If applicable | If applicable | Yes
58 | EMC Test Reports (if project-specific) | Inspection & Test Records | If tested | Conducted/radiated; immunity | F | If applicable | If applicable | If applicable | Yes
59 | Pre-delivery Inspection (PDI) Checklist & Photos | Inspection & Test Records | All | Internal photos, labels, marking, wiring tidiness | F | Yes | No | Yes | Yes
60 | As-built Cable/Termination Test Reports | Inspection & Test Records | If specified | Continuity, insulation; fiber OTDR if required | F | If applicable | If applicable | If applicable | Yes
61 | System Backup Images & Configuration Files | Software & Integration | All | Controller/servers/HMIs; restore instructions | F | Yes | No | Yes | Yes
62 | Version List (HW/FW/SW) & Patch Levels | Software & Integration | All | Per cabinet/module/server with serials | F | Yes | No | Yes | Yes
63 | License Keys/Dongles Report | Software & Integration | All | Counts, expiry, media | F | Yes | No | Yes | Yes
64 | OPC/Modbus/Protocol Mapping & Tag List | Software & Integration | All | Data points, scaling, status bits | F | Yes | No | Yes | Yes
65 | IOM Manuals — Controllers/Servers/Networks/Cabinets | Manuals & Training | All | Install, operation, maintenance | F | Yes | No | Yes | Yes
66 | Cybersecurity Hardening Guide (site) | Manuals & Training | All | Accounts, services, firewall rules, whitelisting | F | Yes | No | Yes | Yes
67 | User Account Management SOP | Manuals & Training | All | Roles, privileges, password policy | F | Yes | No | Yes | Yes
68 | Maintenance & Troubleshooting Manual | Manuals & Training | All | Fault isolation, spares, diagnostics | F | Yes | No | Yes | Yes
69 | Training Plan & Materials (Operator/Maintenance) | Manuals & Training | All | Agendas, handouts, attendance | F | If applicable | If applicable | If applicable | Yes
70 | Recommended Spare Parts List & MTBF Data | Manuals & Training | All | Critical spares, quantities | F | Yes | No | Yes | Yes
71 | As-built Drawings — GA/Wiring/Network/Power | As-built & Close-out | All | PDF + native files | F | Yes | No | Yes | Yes
72 | Final I/O List & Cross-Reference | As-built & Close-out | All | Terminals/channels vs tag list | F | Yes | No | Yes | Yes
73 | Final Configuration Report (modules/controllers/servers) | As-built & Close-out | All | Slots, options, firmware; serials | F | Yes | No | Yes | Yes
74 | Serial Number-to-Tag/Cabinet Cross-Reference | As-built & Close-out | All | Include firmware versions | F | Yes | No | Yes | Yes
75 | Warranty Certificates | As-built & Close-out | All | Coverage & start date | F | Yes | No | Yes | Yes
76 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files | F | Yes | No | Yes | Yes
77 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
78 | Preservation & Packing Records with Photos | Packing & Logistics | All | Desiccants, tilt/shock indicators, rack mounting protections | F | Yes | No | Yes | Yes
79 | Shipping & Handling Instructions | Packing & Logistics | All | Lifting/handling, storage, shipping marks | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — System Cabinets (DCS / IPS / F&G) VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the scope requires (e.g., Ex interfaces, IPS/SIS in scope, F&G panels, seismic qualification).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: system architecture, cabinet GA, I/O count & spares, power/heat calcs, network plan, compliance matrix, alarm/HMI philosophies, redundancy configuration, and environmental/EMC declarations.
4) Standards reference (typical): IEC 61508 (logic solver), IEC 61511 (SIS lifecycle), NFPA 72 / EN 54 (F&G panels), IEC 62443 (OT cybersecurity), IEC 61326/61000-6-x (EMC), IEC 60529 (IP), IEC 60068 (environmental), AS/NZS/IEEE/IEC seismic as specified.
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Architecture/drawings/calcs — 3–5 weeks; FAT/iFAT procedures — 4 weeks; Final records — prior to shipment.
6) MRB content should include: FAT/iFAT/SAT reports, network/performance/soak tests, conformance certificates (SIL/EMC/IP/Ex as applicable), backup images & version lists, manuals & cybersecurity guides, as-built drawings & I/O lists, and packing list.