## RTD_TC Element VDR
Vendor Document Requirement (VDR) — Temperature Element (RTD / Thermocouple) — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. calibration & witness points | Project Admin & Planning | All | Include RTD/TC calibration, insulation resistance, continuity/polarity checks | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and submission plan | R | Yes | No | Yes | No
5 | Nonconformance/Concession/Deviation & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Instrument Datasheet — Temperature Element (per tag) | Design & Engineering | All | RTD: Pt100/Pt1000, Class A/B (IEC 60751), 2/3/4-wire, α=0.00385; TC: Type K/J/T/N/E/R/S/B (IEC 60584-1/ASTM E230), junction (grounded/isolated), polarity; sheath OD/length, temp range, head type, process connection | R | Yes | Yes | Yes | Yes
7 | Thermowell Datasheet (if applicable) | Design & Engineering | If thermowell supplied | Type (flanged/threaded/vanstone), material, PWHT/CRA cladding if any, insertion length U, tip shape (taper/straight/step), surface finish, corrosion allowance | R | If applicable | Yes | If applicable | Yes
8 | Thermowell Wake Frequency & Stress Calculations | Design & Engineering | If thermowell supplied | Per ASME PTC 19.3 TW-2016 (or project spec): natural frequency, Strouhal, max velocity, static/dynamic stress, fatigue | R | If applicable | Yes | If applicable | Yes
9 | General Arrangement Drawing — Temperature Element | Design & Engineering | All | Sheath OD/length, hot junction/tip style, lead exit, head/terminal block, cable/MI type, gland | R | Yes | Yes | Yes | Yes
10 | General Arrangement Drawing — Thermowell | Design & Engineering | If thermowell supplied | Face-to-face, connection details, bore, taper, U/L dimensions, stamping/marking | R | If applicable | Yes | If applicable | Yes
11 | Detail Drawing(s) with Tolerances — Element &/or Thermowell | Design & Engineering | All | Critical dims, concentricity, finish, tip clearance to bottom of well | R | Yes | Yes | Yes | Yes
12 | Materials of Construction List (wetted & non-wetted) | Design & Engineering | All | Sheath (SS316L/310/Hastelloy), thermowell material, head/housing, seals/elastomers, extension leads/insulation | R | Yes | Yes | Yes | Yes
13 | Extension Cable / MI Cable Specification | Design & Engineering | If cable supplied | MI cable grade, insulation (MgO), sheath, color code; extension lead insulation (PTFE/FEP/fiberglass), max length | R | If applicable | If applicable | If applicable | Yes
14 | Compliance Matrix to Project Specification / Datasheet | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
15 | Calibration Procedure — RTD / Thermocouple | Procedures & QC | All | Traceable to ISO/IEC 17025; reference bath/comparator; points across range; ITS-90 coefficients (RTD); EMF table basis (TC) | R | Yes | If applicable | Yes | Yes
16 | Insulation Resistance (IR) Test Procedure | Procedures & QC | All | Test voltage (e.g., 100 VDC), min MΩ at ambient and elevated temp | R | Yes | If requested | Yes | Yes
17 | Continuity & Polarity Check Procedure (TC) / Lead Wire Verification (RTD) | Procedures & QC | All | 2/3/4-wire verification; TC polarity per IEC color code | R | Yes | If requested | Yes | Yes
18 | PMI Procedure for Alloy Verification | Procedures & QC | If specified | Thermowell/sheath materials | R | If applicable | If applicable | If applicable | Yes
19 | Welding Procedure & Quals (WPS/PQR/WPQR) — Thermowell | Procedures & QC | If fabricated thermowell | Include NDE hold points | R | If applicable | If applicable | If applicable | Yes
20 | NDE Procedures (VT/PT/RT/UT) — Thermowell | Procedures & QC | If fabricated thermowell | Coverage and acceptance criteria | R | If applicable | If applicable | If applicable | Yes
21 | Hydro/Pressure Test Procedure — Thermowell | Procedures & QC | If pressure test specified | Medium, pressure, duration, acceptance | R/W | If applicable | If applicable | If applicable | Yes
22 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | End caps, desiccant, MI cable sealing, glass bead avoidance; O2 cleaning if specified | R | Yes | No | Yes | Yes
23 | IEC 60751 Conformance Statement (RTD) | Compliance & Certifications | If RTD supplied | Class A/B (or project class), ITS-90 coefficients, R0 value | F | If applicable | Yes | If applicable | Yes
24 | IEC 60584-1 / ASTM E230 Conformance Statement (TC) | Compliance & Certifications | If TC supplied | Type K/J/T/N/E/R/S/B; class/limits of error | F | If applicable | Yes | If applicable | Yes
25 | Hazardous Area Certificates (ATEX/IECEx) + Schedules | Compliance & Certifications | If Ex area | Ex i/Ex d parameters; temperature class; installation conditions | R/F | If applicable | If applicable | If applicable | Yes
26 | Ingress Protection (IP66/67) Statement — Head/Enclosure | Compliance & Certifications | If head/enclosure supplied | IEC 60529 | F | If applicable | If applicable | If applicable | Yes
27 | PED/UKCA/CE Declaration (as applicable) | Compliance & Certifications | If thermowell pressure accessory | Category/Module or SEP | F | If applicable | If applicable | If applicable | Yes
28 | NACE MR0175/ISO 15156 Compliance (wetted metallics) | Compliance & Certifications | If sour service | Thermowell/sheath/fasteners (wetted) | F | If applicable | If applicable | If applicable | Yes
29 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | If applicable | If applicable | Yes
30 | Mill Test Certificates (EN 10204 3.1) — wetted metallics | Materials & Special Service | Thermowell/sheath | Bar/forging/tube certificates; fasteners | F | If applicable | If applicable | If applicable | Yes
31 | Elastomer/Polymer Compliance (FDA/WRAS if required) | Materials & Special Service | If specified | Gaskets/seals approvals | F | If applicable | If applicable | If applicable | Yes
32 | Calibration Certificate (as-left) — RTD | Inspection & Test Records | If RTD supplied | R0 at 0°C, α, ITS-90 coefficients (A,B,C); points across range; expanded uncertainty | F/W | If applicable | No | If applicable | Yes
33 | Calibration Certificate (as-left) — Thermocouple | Inspection & Test Records | If TC supplied | EMF vs temp points; limits of error class; expanded uncertainty | F/W | If applicable | No | If applicable | Yes
34 | Insulation Resistance (IR) Test Record | Inspection & Test Records | All | Measured MΩ at specified V and temp | F | Yes | No | Yes | Yes
35 | Continuity/Polarity & Lead Verification Record | Inspection & Test Records | All | 2/3/4-wire verification; TC polarity per IEC code | F | Yes | No | Yes | Yes
36 | Dimensional Inspection Report — Element | Inspection & Test Records | All | Sheath OD/length, tip details, head thread/entries | F | Yes | No | Yes | Yes
37 | Dimensional Inspection Report — Thermowell | Inspection & Test Records | If thermowell supplied | Bore, U/L, taper/step, runout, concentricity | F | If applicable | No | If applicable | Yes
38 | NDE Reports (VT/PT/RT/UT) — Thermowell | Inspection & Test Records | If fabricated thermowell | Welds & critical areas | F | If applicable | No | If applicable | Yes
39 | Hydro/Pressure Test Certificate — Thermowell | Inspection & Test Records | If required | Pressure, duration, acceptance | F/W | If applicable | No | If applicable | Yes
40 | PMI Reports — Alloy Verification | Inspection & Test Records | If specified | Materials tested and results | F | If applicable | No | If applicable | Yes
41 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
42 | Head-mounted Transmitter Datasheet & Configuration | Software & Integration | If transmitter supplied | Input type, ranges, output, damping, sensor matching/Callendar–Van Dusen or TC type selection | R | If applicable | If applicable | If applicable | Yes
43 | EDD/DTM/Device Files & Version List | Software & Integration | If smart transmitter | Provide files and version compatibility matrix | F | If applicable | If applicable | If applicable | Yes
44 | Communication Conformance Certificate (HART/FF/PA) | Software & Integration | If digital comms | FieldComm Group/PI conformance | R/F | If applicable | If applicable | If applicable | Yes
45 | Host System Integration Notes | Software & Integration | If transmitter supplied | DCS/AMS/PRM/800xA/FDM compatibility and parameters | F | If applicable | If applicable | If applicable | Yes
46 | Installation, Operation & Maintenance (IOM) Manual — Element/Thermowell | Manuals & Installation | All | Insertion depth, spring-loading or spacing to well bottom, torque, sealing, cold junction considerations (TC) | F | Yes | If requested | Yes | Yes
47 | Wiring Diagrams — 2/3/4-wire RTD & TC Color Codes | Manuals & Installation | All | Per IEC 60751/IEC 60584 regional color code; terminal mapping | F | Yes | If requested | Yes | Yes
48 | Storage & Handling Instructions | Manuals & Installation | All | Moisture control for MI cable, end-cap sealing, transport protection | F | Yes | No | Yes | Yes
49 | As-built Tag List & Configuration (per tag) | As-built & Close-out | All | Element type, class, length, sheath OD, wiring, head type; transmitter config if supplied | F | Yes | No | Yes | Yes
50 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include model code; transmitter serial/firmware if applicable | F | Yes | No | Yes | Yes
51 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
52 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
53 | Preservation & Packing Records with Photos | Packing & Logistics | All | End caps, desiccant, sealing of MI cable, protective tubes for long elements | F | Yes | No | Yes | Yes
54 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, max bundle lengths, lifting/handling cautions | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Temperature Element (RTD/TC) VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., Ex area, thermowell supplied, sour service).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Temperature element datasheet, (thermowell datasheet and ASME PTC 19.3 TW calc if in scope), GA drawings, materials list, compliance matrix, and IEC 60751/IEC 60584 conformance statements.
4) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/config docs — 3–4 weeks; Final records — prior to shipment.
5) MRB content should include: calibration certificates (RTD/TC), IR & continuity/polarity records, dimensional reports, thermowell NDE/pressure tests (if applicable), conformance & material certificates, manuals, as-built lists, and packing list.