## Temperature Transmitter VDR
Vendor Document Requirement (VDR) — Temperature Transmitter — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. calibration & witness points | Project Admin & Planning | All | Include sensor simulation, loop test, diagnostics/NE107 checks | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and submission plan | R | Yes | No | Yes | No
5 | Nonconformance/Concession/Deviation & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Instrument Datasheet — Temperature Transmitter (per tag) | Design & Engineering | All | Input type(s) RTD/TC/mV/Ω, ranges, output (4–20 mA/HART/FF/PA/Modbus), power, Ex rating if any | R | Yes | Yes | Yes | Yes
7 | Configuration / Range Sheet | Design & Engineering | All | Sensor type & wiring (2/3/4-wire), LRV/URV, units, damping/filters, upscale/downscale failsafe, CJ compensation (TC) | R | Yes | Yes | Yes | Yes
8 | Accuracy & Stability Statement | Design & Engineering | All | Reference accuracy, long-term stability, temperature effect, total probable error | R | Yes | Yes | Yes | Yes
9 | Sensor Matching / Callendar–Van Dusen (RTD) or TC Linearization Details | Design & Engineering | If sensor matching used | R0, α, A/B/C coefficients; EMF tables; lead-wire compensation method | R | If applicable | If applicable | If applicable | Yes
10 | General Arrangement (GA) — Head-mounted Transmitter | Design & Engineering | If head-mount | Terminal layout, entry sizes, enclosure type, IP rating, mounting in DIN Form A head | R | If applicable | If applicable | If applicable | Yes
11 | General Arrangement (GA) — Rail-mounted Transmitter | Design & Engineering | If rail-mount | DIN rail footprint, terminals, enclosure rating | R | If applicable | If applicable | If applicable | Yes
12 | Wiring Diagram & Terminal Mapping | Design & Engineering | All | 2/3/4-wire RTD, TC polarity, outputs, shields/earths | R | Yes | Yes | Yes | Yes
13 | Materials of Construction List (enclosure, terminals, seals) | Design & Engineering | All | Housing, terminal metallurgy/plating, gasket/elastomers, potting | R | Yes | Yes | Yes | Yes
14 | Compliance Matrix to Project Specs / Datasheet | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
15 | Calibration / Configuration Procedure | Procedures & QC | All | Traceable references; sensor simulation steps; 4–20 mA trim; HART/FF write-lock use | R | Yes | If requested | Yes | Yes
16 | Functional Test & Diagnostics Procedure (incl. NE107) | Procedures & QC | All | Sensor break/short detection, upscale/downscale behavior, cold-junction check (TC), damping/filter tests | R | Yes | If requested | Yes | Yes
17 | Environmental / Burn-in / Temperature Soak Procedure | Procedures & QC | If specified | Soak profile and acceptance criteria | R | If applicable | No | If applicable | Yes
18 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | ESD handling, moisture barriers, desiccant, caps | R | Yes | No | Yes | Yes
19 | Software/Firmware Handling & Cybersecurity Hardening Guide | Procedures & QC | All smart devices | Default credentials, write lock/security switch, firmware update policy | R | Yes | No | Yes | Yes
20 | Hazardous Area Certificates (ATEX/IECEx) + Schedules | Compliance & Certifications | If Ex required | Entity parameters, temp class, EPL/Zone, installation conditions | R/F | If applicable | If applicable | If applicable | Yes
21 | EMC/EMI Compliance Statement | Compliance & Certifications | All | IEC 61326 series (industrial) | F | Yes | Yes | Yes | Yes
22 | Electrical Safety (IEC 61010-1) Declaration | Compliance & Certifications | All | Safety of electrical equipment | F | Yes | Yes | Yes | Yes
23 | Ingress Protection (IP66/67) Compliance Statement | Compliance & Certifications | If enclosed | IEC 60529 | F | If applicable | If applicable | If applicable | Yes
24 | Functional Safety (IEC 61508) SIL Certificate & Safety Manual | Compliance & Certifications | If used in SIS | SIL capability, SFF, PFDavg assumptions; provide Safety Manual | R/F | If applicable | If applicable | If applicable | Yes
25 | Field Communication Conformance Certificate (HART/FF/Profibus PA) | Compliance & Certifications | Digital comms devices | FieldComm Group/PI certificate or test report | R/F | If applicable | Yes | If applicable | Yes
26 | CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | DoC listing directives/standards | F | If applicable | Yes | If applicable | Yes
27 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | No | If applicable | Yes
28 | Calibration Certificate (as-left) — Loop/Output | Inspection & Test Records | All | At range points; expanded uncertainty; reference instruments list | F/W | Yes | No | Yes | Yes
29 | Functional Test Report & Diagnostics Results | Inspection & Test Records | All | Sensor break/short, upscale/downscale, CJ accuracy (TC), NE107 states | F | Yes | No | Yes | Yes
30 | Environmental/Burn-in Test Record | Inspection & Test Records | If specified | Soak results and acceptance | F | If applicable | No | If applicable | Yes
31 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
32 | EDD/DTM/Device Files & Version List | Software & Integration | Smart devices | Provide files and version compatibility matrix | F | Yes | No | Yes | Yes
33 | GSD/EDS/CFH files (Profibus PA/FF) | Software & Integration | If FF/PA used | Node defaults, function blocks | F | If applicable | If applicable | If applicable | Yes
34 | Modbus/HART Variable Map & Scaling | Software & Integration | If Modbus/HART used | Variables, units, ranges, status bits | F | If applicable | If applicable | If applicable | Yes
35 | Firmware Revision Report & Release Notes | Software & Integration | All | Device firmware per serial; known issues/mitigations | F | Yes | No | Yes | Yes
36 | Host System Integration Notes | Software & Integration | All | DCS/AMS/PRM/800xA/FDM compatibility and parameter settings | F | Yes | No | Yes | Yes
37 | Installation, Operation & Maintenance (IOM) Manual | Manuals & Installation | All | Mounting, wiring, shielding/earthing, CJ considerations, write-lock/security | F | Yes | If requested | Yes | Yes
38 | Safety Manual (IEC 61508) | Manuals & Installation | If SIS | Proof-test intervals, failure modes, restrictions | F | If applicable | If applicable | If applicable | Yes
39 | Quick Start / Configuration Guide | Manuals & Installation | All | Default ranges, addressing, write protection | F | Yes | If requested | Yes | Yes
40 | Storage & Handling Instructions | Manuals & Installation | All | ESD handling, moisture protection | F | Yes | No | Yes | Yes
41 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | Input type, wiring, LRV/URV, units, damping/filters, output mode, address | F | Yes | No | Yes | Yes
42 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include year/week code, firmware version | F | Yes | No | Yes | Yes
43 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
44 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
45 | Preservation & Packing Records with Photos | Packing & Logistics | All | ESD protection, desiccant, shock indicators if specified | F | Yes | No | Yes | Yes
46 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, handling cautions | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Temperature Transmitter VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., Ex area, SIS use, rail vs head mount).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Transmitter datasheet & configuration, accuracy/stability statement, GA/wiring, materials list, compliance matrix, EMC/Safety/IP declarations, and comms conformance certificates (HART/FF/PA as applicable).
4) If SIS: include IEC 61508 SIL certificate + Safety Manual; ensure diagnostics/NE107 mapping is documented.
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/config docs — 3–4 weeks; Final records — prior to shipment.
6) MRB content should include: calibration & functional test records, conformance certificates, manuals, firmware/version report, as-built configuration per tag, and packing list.