## Ultrasonic Level VDR
Vendor Document Requirement (VDR) — Ultrasonic Level Transmitter — InstruNexus
Seq | Deliverable | Category | Applicability | Standard/Notes | Submission Purpose (R/W/F) | Required? | Required along with Bid | To Submit after PO | Part of MRB | Vendor Document No. | First Submittal Due (wks from PO) | Revision | Submission Date | Client Action (A/Revise/Comment) | Final Status | Remarks
1 | Supplier Document Register/List (SDRL) | Project Admin & Planning | All |  | R | Yes | No | Yes | No
2 | Project Quality Plan (PQP) / Quality Management Plan | Project Admin & Planning | All | Align with ISO 9001 supplier QMS | R | Yes | No | Yes | Yes
3 | Inspection & Test Plan (ITP) incl. functional & witness points | Project Admin & Planning | All | Include functional test, echo-curve capture, configuration lock checks | R/W | Yes | If requested | Yes | Yes
4 | Manufacturing / Assembly Schedule | Project Admin & Planning | All | Milestones and document submittal plan | R | Yes | No | Yes | No
5 | Nonconformance/Concession/Deviation & Corrective Action templates | Project Admin & Planning | All |  | R | Yes | No | Yes | No
6 | Instrument Datasheet — Ultrasonic Level Transmitter (per tag) | Design & Engineering | All | Range, frequency, beam angle, blanking distance, temp comp method, outputs/comms, Ex rating | R | Yes | Yes | Yes | Yes
7 | Application & Sizing Check | Design & Engineering | All | Tank geometry, obstructions, nozzle length/ID, foam/dust/vapor/agitator effects, ambient extremes | R | Yes | Yes | Yes | Yes
8 | Accuracy, Repeatability & Response Statement | Design & Engineering | All | Reference accuracy, resolution, response time, beam divergence impact | R | Yes | Yes | Yes | Yes
9 | Transducer/Converter GA & Wiring Diagram | Design & Engineering | All | Terminals, entry sizes, enclosure rating, earthing/shielding, cable spec | R | Yes | Yes | Yes | Yes
10 | Mounting Nozzle/Standpipe Details (if used) | Design & Engineering | If standpipe/nozzle used | ID, length, chamfer, smooth bore (no corrugations), alignment, purge/drain | R | If applicable | If applicable | If applicable | Yes
11 | False Echo Mapping / Obstruction Handling Plan | Design & Engineering | All | Nozzle/ladder/internal obstructions, echo suppression settings, baseline capture | R | Yes | Yes | Yes | Yes
12 | Temperature & Sound-speed Compensation Method | Design & Engineering | All | Integral sensor or remote RTD; algorithm details; humidity/gas composition notes | R | Yes | Yes | Yes | Yes
13 | Materials of Construction List (sensor face, enclosure, seals) | Design & Engineering | All | PVDF/PTFE/ETFE face, housing alloy/polymer, window, gasket/elastomers | R | Yes | Yes | Yes | Yes
14 | Environmental Limits & Derating Curves | Design & Engineering | All | Ambient/temp limits, vibration, UV/sun, IP rating scope, max vapour temperature | R | Yes | Yes | Yes | Yes
15 | Compliance Matrix to Project Specs / Datasheet | Design & Engineering | All | Point-by-point compliance; list deviations | R | Yes | Yes | Yes | Yes
16 | Functional Test & Configuration Procedure | Procedures & QC | All | Simulation/reference distance checks; range set; damping/filters; NE43/NE107 | R | Yes | If requested | Yes | Yes
17 | Bench Verification Procedure — Distance/Output | Procedures & QC | All | Reference targets at multiple distances; error vs acceptance | R | Yes | If requested | Yes | Yes
18 | Echo Quality/AGC Verification Procedure | Procedures & QC | All | Echo confidence, SNR, AGC behavior across range | R | Yes | If requested | Yes | Yes
19 | Cleaning, Preservation & Packing Procedure | Procedures & QC | All | Sensor face protection, desiccants, caps; ESD handling for electronics | R | Yes | No | Yes | Yes
20 | Software/Firmware Handling & Cybersecurity Guide | Procedures & QC | Smart transmitters | Default passwords, write lock/security switch, update policy | R | Yes | No | Yes | Yes
21 | Hazardous Area Certificates (ATEX/IECEx) + Schedules | Compliance & Certifications | If Ex required | Entity parameters, temp class, EPL/Zone, install conditions | R/F | If applicable | If applicable | If applicable | Yes
22 | EMC/EMI Compliance Statement (IEC 61326) | Compliance & Certifications | All | Industrial environment | F | Yes | Yes | Yes | Yes
23 | Electrical Safety (IEC 61010-1) Declaration | Compliance & Certifications | All | Safety of electrical equipment | F | Yes | Yes | Yes | Yes
24 | Ingress Protection (IP66/67) Compliance Statement | Compliance & Certifications | All | IEC 60529 | F | Yes | Yes | Yes | Yes
25 | Functional Safety (IEC 61508) — SIL Certificate & Safety Manual | Compliance & Certifications | If used in SIS | SIL capability, SFF, PFDavg assumptions | R/F | If applicable | If applicable | If applicable | Yes
26 | CE/UKCA Declaration (as applicable) | Compliance & Certifications | Jurisdiction dependent | DoC listing standards/directives | F | If applicable | If applicable | If applicable | Yes
27 | RoHS/REACH or regional material compliance | Compliance & Certifications | If contract requires |  | F | If applicable | If applicable | If applicable | Yes
28 | Materials Certificates / CoC — Sensor Face & Wetted Fasteners | Materials & Special Service | If specified | EN 10204 3.1 for metals; CoC for polymers | F | If applicable | If applicable | If applicable | Yes
29 | Elastomer/Polymer Compliance (FDA/WRAS if required) | Materials & Special Service | If hygienic or specified | Gaskets/seals approvals | F | If applicable | If applicable | If applicable | Yes
30 | Functional Test Report & Configuration As-left | Inspection & Test Records | All | Range, damping, filters, output checks, address; NE43/NE107 | F | Yes | No | Yes | Yes
31 | Echo Curve / Baseline Diagnostic Capture | Inspection & Test Records | All | Saved trace at shipment; false echo map if applied | F/W | Yes | No | Yes | Yes
32 | Accuracy/Distance Verification Record | Inspection & Test Records | All | Measured error at multiple distances vs acceptance | F | Yes | No | Yes | Yes
33 | Temperature Compensation Verification Record | Inspection & Test Records | All | Compensated vs uncompensated distance check | F | If applicable | No | If applicable | Yes
34 | Gauge & Calibrator Certificates used for tests | Inspection & Test Records | All | Traceability chain with due dates | F | Yes | No | Yes | Yes
35 | EDD/DTM/Device Files & Version List | Software & Integration | Smart devices | Provide files and compatibility matrix | F | Yes | No | Yes | Yes
36 | Communication Conformance Certificate (HART/FF/PA) | Software & Integration | Digital comms devices | FieldComm Group/PI conformance | R/F | If applicable | If applicable | If applicable | Yes
37 | Modbus/HART Variable Map & Scaling | Software & Integration | If Modbus/HART used | Variables, units, status bits, diagnostics/echo export | F | If applicable | If applicable | If applicable | Yes
38 | Firmware Revision Report & Release Notes | Software & Integration | All smart devices | Device firmware per serial; known issues/mitigations | F | Yes | No | Yes | Yes
39 | Host System Integration Notes | Software & Integration | All | DCS/AMS/PRM/800xA/FDM compatibility and parameters | F | Yes | No | Yes | Yes
40 | Installation, Operation & Maintenance (IOM) Manual | Manuals & Installation | All | Nozzle guidelines, blocking distance/near-zone, false echo mapping, alignment, wiring | F | Yes | If requested | Yes | Yes
41 | Mounting Templates & Clearance Drawings | Manuals & Installation | All | Clearance envelope; recommended nozzle IDs/lengths; aiming brackets | F | Yes | If requested | Yes | Yes
42 | Storage & Handling Instructions | Manuals & Installation | All | Sensor face protection, moisture/temperature limits | F | Yes | No | Yes | Yes
43 | As-built Configuration & Parameter List (per tag) | As-built & Close-out | All | Range, units, damping, blanking distance, filters, echo map enabled, comm address | F | Yes | No | Yes | Yes
44 | Serial Number-to-Tag Cross-Reference List | As-built & Close-out | All | Include model code and firmware version | F | Yes | No | Yes | Yes
45 | Final Data Book / Manufacturer’s Record Book (MRB) | As-built & Close-out | All | Indexed PDF with bookmarks + native files as applicable | F | Yes | No | Yes | Yes
46 | Packing List & Country of Origin (if required) | As-built & Close-out | All |  | F | Yes | No | Yes | Yes
47 | Preservation & Packing Records with Photos | Packing & Logistics | All | Sensor face protected; desiccants; shock/humidity indicators if specified | F | Yes | No | Yes | Yes
48 | Shipping & Handling Instructions | Packing & Logistics | All | Orientation, handling, recommissioning steps | F | Yes | No | Yes | Yes

## Legend & Instructions
Legend & Instructions — Ultrasonic Level Transmitter VDR
How to Use
1) Vendor to submit all items marked 'Required? = Yes'. Items marked 'If applicable' apply when the service/scope requires (e.g., Ex area, SIS use, standpipe/nozzle mounting, hygienic service).
2) R/W/F codes: R = For Review/Approval prior to manufacture; W = Hold/Witness point per ITP; F = For Records at final handover.
3) Typical bid-stage inclusions: Datasheet, Application & sizing check, Accuracy/response statement, GA & wiring, Materials list, Environmental/derating limits, False-echo mapping plan, Compliance matrix, and EMC/Safety/IP declarations; Ex/SIL as applicable.
4) Installation cautions: observe blocking distance and beam angle; avoid corrugated/rough standpipes; map false echoes after install; consider foam/vapor/temperature effects on speed of sound—use temperature compensation and, if needed, choose alternate technology (e.g., GWR) when ultrasonic limits are exceeded.
5) Suggested due dates from PO: SDRL/PQP/ITP — 2 weeks; Drawings/config docs — 3–4 weeks; Final records — prior to shipment.
6) MRB content should include: functional test & echo curve, accuracy/distance verification, temp-comp verification (if used), conformance certificates (Ex/IP/EMC as applicable), materials certificates (if specified), manuals, as-built configuration, and packing list.