## DP Level Transmitter
Pre‑Commissioning Checklist – DP Level Transmitter
Project Name:
Location:
Instrument Tag:
Instrument Type: |  | DP Level Transmitter
Prepared By:
Checked By:
Approved By:
Date: |  | 2025-09-01
Activity Category | Checklist Item | Completed | Remarks
Documentation Verification | Verify tag vs. P&ID and instrument index
Documentation Verification | Check datasheet vs. installed transmitter
Documentation Verification | Review calibration certificate
Documentation Verification | Confirm vendor drawing orientation
Documentation Verification | Check impulse line material certificate
Mechanical Installation | Verify tapping points location vs. P&ID
Mechanical Installation | Check impulse line slope (min 1:10)
Mechanical Installation | Ensure equal impulse line length
Mechanical Installation | Confirm manifold installation
Mechanical Installation | Check drain/vent valves operable
Mechanical Installation | Verify supports and clamps installed
Mechanical Installation | Inspect flange gaskets alignment
Electrical & Cabling | Check power supply connection
Electrical & Cabling | Verify polarity and grounding
Electrical & Cabling | Inspect junction box tagging
Electrical & Cabling | Confirm cable gland sealing
Electrical & Cabling | Verify shielding continuity
Calibration / Configuration | Set zero suppression/elevation
Calibration / Configuration | Verify span setting vs. design range
Calibration / Configuration | Simulate DP signal and check DCS response
Calibration / Configuration | Check alarm settings (HH, LL)
Calibration / Configuration | Verify NAMUR NE43 fail-safe configuration
Functional & Safety Checks | Perform loop check to DCS
Functional & Safety Checks | Verify trend stability
Functional & Safety Checks | Check leak test of impulse lines
Functional & Safety Checks | Confirm hazardous area compliance
Functional & Safety Checks | Close punch list items
© Instrunexus ¦ www.instrunexus.com