## Orifice DP Flow PreComm
Pre‑Commissioning Checklist – Orifice Plate & DP Flow
Project Name:
Location:
Instrument Tag:
Instrument Type: |  | Orifice Plate + DP Flow Transmitter
Prepared By:
Checked By:
Approved By:
Date: |  | 2025-09-01
Activity Category | Checklist Item | Completed | Remarks
Documentation Verification | Verify instrument tag against P&ID and instrument index
Documentation Verification | Check calibration and inspection certificates for orifice plate
Documentation Verification | Verify DP transmitter datasheet range vs. design differential
Documentation Verification | Confirm orifice plate bore size and beta ratio vs. datasheet
Documentation Verification | Review vendor drawings for installation orientation
Orifice Plate Inspection | Check orifice plate material and thickness against datasheet
Orifice Plate Inspection | Verify orifice plate edge condition (sharp, no damage/burrs)
Orifice Plate Inspection | Check correct orientation of plate (bevel upstream for concentric plates)
Orifice Plate Inspection | Confirm tag number and flow direction arrow engraved on plate/carrier
Orifice Plate Inspection | Verify plate centering within orifice fitting/pipe bore
Mechanical Installation | Verify straight run pipe lengths upstream and downstream as per standard
Mechanical Installation | Check correct gasket alignment and proper bolt torque on orifice flanges
Mechanical Installation | Confirm tapping orientation and elevation as per drawing
Mechanical Installation | Inspect impulse line slope (minimum 1:10) and equal lengths where required
Mechanical Installation | Check impulse line flushing, cleanliness, and absence of leaks
Mechanical Installation | Ensure proper supports and clamps for impulse lines
Mechanical Installation | Verify manifold (3-valve/5-valve) installation and accessibility
Mechanical Installation | Confirm drain/vent connections are provided and operable
Electrical & Impulse Lines | Check electrical wiring and polarity as per diagram
Electrical & Impulse Lines | Verify power supply to DP transmitter
Electrical & Impulse Lines | Check grounding and shielding continuity
Electrical & Impulse Lines | Inspect cable gland sealing and termination quality
Electrical & Impulse Lines | Verify junction box ferrules and tagging
Electrical & Impulse Lines | Confirm impulse lines are heat-traced/insulated if required
Loop & Signal Checks | Perform loop check from DP transmitter to DCS/PLC
Loop & Signal Checks | Verify 4–20 mA/HART/Fieldbus signal communication
Loop & Signal Checks | Check zero/span calibration against design DP range
Loop & Signal Checks | Simulate DP signal and verify flow indication in DCS
Loop & Signal Checks | Check low-flow cut-off configuration if applicable
Loop & Signal Checks | Verify pulse/totalizer output scaling if used
Loop & Signal Checks | Check signal stability and noise on DCS trend
Functional & Safety Checks | Verify process isolation valves operation
Functional & Safety Checks | Leak test impulse lines and manifold connections
Functional & Safety Checks | Ensure hazardous area compliance (Ex-proof/IS)
Functional & Safety Checks | Check transmitter fail-safe settings (NAMUR NE43)
Functional & Safety Checks | Confirm proper tagging and labeling of transmitter and manifold
Functional & Safety Checks | Perform final walkdown and close punch list items
© Instrunexus ¦ www.instrunexus.com